Concealed Bulkhead Active Chilled Beams

# PART 1 – GENERAL

## RELATED DOCUMENTS

The requirements of the General Conditions, Supplementary Conditions and the following specification sections apply to all work herein:

1.	(list related documents here)

## SUMMARY

Furnish and install Dadanco ACB10 concealed bulkhead active chilled beam units herein specified and as the lengths and quantities indicated on the Drawings.

## REFERENCE STANDARDS

ASTM-653
ASTM-C1071-05
ASTM-E84 25/50
UL 94 V-0
UL 2043
UL 181
ASHRAE 200
ASHRAE 62-2001

## SUBMITTALS AND PROPOSALS

The following submittal data shall be furnished according to General Conditions and Section 15 - - - and shall include, but not be limited to:

A.	Performance Data:

1.	Sensible cooling capacities based on room conditions [BTUH]
2.	Latent cooling capacities based on room conditions [BTUH]
3.	Heating capacities (where applicable) [BTUH]
4.	Primary, induced and total airflow rates [CFM]
5.	Airside pressure loss [in H2O]
6.	Chilled and hot water flow rates [GPM]
7.	Waterside pressure loss [ft H2O]
8.	Supply air leaving temperature (primary + induced) in cooling and (where applicable) heating operation [oF]
9. 	Sound pressure levels expressed in NC including 10 dB room absorption [NC]
10.	Sound power levels in octave bands [125Hz – 4KHz dB]

B.	Mechanical Data

1.	Unit weights and dimensions
2.	Mounting bracket detail
3.	Manufacturers recommendations for installation

## 1.05	WARRANTY

Comply with the requirements of the General Conditions and Section 15 - - -

# PART 2 - PRODUCTS

## 2.01	ACCEPTABLE MANUFACTURERS

If it complies with these Specifications, active chilled beams manufactured by one of the following manufacturers will be acceptable:

1.	Dadanco

## 2.02	CONCEALED BULKHEAD ACTIVE CHILLED BEAM UNITS

A.	Active chilled beam units shall be as indicated on the Mechanical and Architectural Drawings and shall meet the capacity and acoustical performance requirements specified and indicated on the schedule and Contract Documents. Cooling and heating performance data shall be based on the installation with a sidewall mounted grille having a maximum airflow resistance of 0.03 in H2O.  Active chilled beam performance data shall be established by testing in accordance to ASHRAE standard 200.

B.	Concealed bulkhead active chilled beams shall be designed for installation into a ceiling bulkhead fitted with separate supply and return air grilles specified on the schedules and drawings. All units shall consist of a casing, primary air plenum, water coil frame and mixing chamber manufactured from 20 GA G-60 galvanized sheet steel conforming to ASTM-653 standards. The primary air plenum shall deliver air through a series of induction nozzles and into a mixing chamber. Secondary air shall be drawn into the underside of the unit through a horizontally mounted water coil and combined with the primary air in the mixing chamber. A single round, oval, or elliptical air connection spigot shall be mounted on the left or right hand side, back, or top of the unit as shown on the Drawings. All sheet metal joints in the primary air plenum and air connection spigot shall be sealed airtight.

C.	Primary air shall be discharged into the mixing chamber through multi-lobed induction nozzles. The size and quantity of nozzles shall be selected to provide the primary and secondary airflows at the inlet static pressure and noise levels specified. Nozzles shall be manufactured from UL 94 V-0 flame retardant thermoplastic.

D.	Concealed bulkhead active chilled beams shall be fitted with a commissioning tube for measuring the static pressure differential between the primary air plenum and the room. Each unit shall be provided with an airflow calibration chart showing primary airflow rate for given nozzle configuration at different static pressures.

E.	Secondary water coils shall be two or four pipe configuration as indicated on the schedules. Coils shall be manufactured with ½” seamless copper tubing with a minimum 0.016” wall thickness mechanically expanded into aluminum fins spaced no closer than 8 FPI (fins per inch). The coils shall have a maximum working pressure of no less than 300 PSI and be 100% factory tested for leakage at 500 PSI. Coil connections shall be ½” O.D. bare copper for field sweating to the water circuit, or threaded fittings, as specified.

F.	Concealed bulkhead active chilled beams shall be delivered to site clean and flushed. Each unit shall be labeled with identification tagging and commissioning requirements for primary air and chilled water flow. Units shall be individually packaged in cardboard cartons and palletized on wooden skids.

G.	The manufacturer shall provide the following options where marked on the Schedules and Drawings:

1.	½“ thick thermal insulation applied to the interior of the primary air plenum to prevent condensation forming on the outside of the unit casing and the interior surfaces of the primary air chamber. Thermal insulation shall be manufactured in accordance with ASTM C1071-05, UL-181 (Air Erosion) and ASTM E84 25/50 (flame spread and smoke density) standards.

2.	Removable lint screen shall be installed on the face of the coil.

3.	Units shall be supplied with either (drainable) drain pans, or non-drainable drip trays, as specified.  Both shall be manufactured from black painted G-60 galvanized steel and sealed water-tight. The drain pans shall be sloped at least 1/8” per foot in accordance with ASHRAE standard 62 and fitted with a plastic capped 5/8” O.D copper drain connection.  The drip drays shall be non-sloped and not include a drain outlet.  If specified, include factory mounted float switches to prevent pan overflow.

3.	½“ NPT male threaded connections fitted to the water coil, suitable for field connection to a ½“ NPT female flexible hose.

4.	½“ NPT female threaded connections fitted to the water coil, suitable for field connection to a ½“ NPT male flexible hose.

H.	The manufacturer shall provide the following accessories where specifically marked on the Schedules and Drawings:

1.	½” Diameter, 18” long flexible hoses comprising of an EPDM lined hose with stainless steel wire braided jacket rated for a maximum operating pressure of not less than 300 PSI at 195°F. Hoses shall be 100% factory tested for leakage.

2.	Galvanized steel round primary air balancing dampers with manual locking quadrant for installation upstream of the active chilled beam.

3.	Provide constant airflow regulators (CAR’s) fitted upstream of the active chilled beam as shown on the Drawings and Schedules. Each regulator shall be preset and factory calibrated to the airflows indicated on the Schedules. Constant airflow regulators shall be provided as an assembly consisting of a UL 94V-0 ABS plastic body housed within a round sleeve for mounting in round duct. Each round sleeve must be fitted with a lip gasket to assure perimeter air tightness with the interior surface of the duct. All regulators must be listed per UL2043 and carry the UL mark indicating compliance. All constant airflow regulators will require no maintenance and must be warranted for a period of no less than five years.

# PART 3 – EXECUTION

## 3.01	INSTALLATION

All active chilled beam units shall be installed in accordance with the latest industry standards, per the manufacturer’s recommendations and as indicated on the Drawings.

A.	Active chilled beams shall be independently suspended from the structure at four points with either ⅜” diameter suspended rods or code approved suspension wire.

B.	Air connections to the main primary air duct shall be made with flexible duct with all joints sealed and made airtight.

C.	The piping system shall be flushed to remove all debris before connecting to the active chilled beams. Water connections shall be flexible hoses or hard connection using sweated fittings.

## 3.02	MOCK-UP INSTALLATION

Prior to installation of multiple active chilled beam units, the Contractor shall install a sample unit as a mock-up generally representative of a typical active chilled beam and ceiling installation. The mock-up installation shall be complete with piping, ductwork and water valves. The mock-up installation shall be located in one of the typical areas of the project. The Contractor shall advise the Engineer and Owners representative after the mock-up is complete and arrange a suitable time for inspection and review to determine any changes and modifications that need to be made for the installation to be acceptable to the Engineer and Owner. The Contractor shall provide the required modifications and additional follow-up field inspections as required without additional cost to the Owner.