Section 23 55 33.16 – *Sample Specification for Sterling GF Gas Fired Unit Heaters*

**PART 1 – GENERAL**

* 1. RELATED DOCUMENTS

1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.
   1. SUMMARY
2. This section includes gas-fired unit heaters
   1. INFORMATIONAL SUBMITTALS
3. Product Data: For each type of gas-fired unit heater indicated. Include rated capacities, operating characteristics, and accessories.
4. Shop Drawings: For gas-fired unit heaters.
   1. Detail equipment assemblies and indicate dimensions, weights, required clearances, components, and location and size of each field connection.
   2. Wiring Diagrams: Power and control wiring.
   3. MAINTENANCE MATERIAL SUBMITTALS
5. Operation and Maintenance Data: For gas-fired unit heaters to include, installation, operation, and maintenance manuals.
   1. QUALITY ASSURANCE
6. Equipment, Electrical Components, Devices, and Accessories: Listed and labeled as defined by Intertek’s ETL certification.
7. Comply with the following codes and standards where applicable:
8. ANSI Z83.8 -2009/CSA 2.6-2009 – American National Standard/CSA Standard for Gas Unit Heaters, Gas Packaged Heaters, Gas Utility Heaters and Gas-Fired Duct Furnaces.
9. ASHRAE/IESNA 90.1-2010 – Applicable requirements in ASHRAE/IESNA 90.1-2010, Section 6 – “Heating, Ventilating, and Air-Conditioning”.
10. NFPA 70, National Electric Code for electrical components and installation.
11. NFPA 54, National Fuel Code for gas components and installation.
    1. WARRANTY
12. Special Warranty: Manufacturer’s standard form in which manufacturer agrees to repair or replace components listed below of gas-fired unit heater that fails in materials or workmanship within the specified warranty period.
13. Warranty Period for Heat Exchangers: Manufacturer’s standard, but not less than 5 years from the date of shipment. Warranty shall be non-prorated.

**PART -2 – PRODUCTS**

1. MANUFACTURES
2. Available Manufacturers: Subject to compliance with requirements, provide products by one of the following or approved equal:
   1. Sterling HVAC Products
   2. (The) Trane Company
   3. Beacon Morris Heating Products
3. Manufacture must have a minimum of 5 year experience manufacturing the products specified in this section.
4. GENERAL
5. Furnish and install, where indicated or scheduled on plans, gas-fired unit heaters. Unit shall be factory assembled, piped and wired, and complying with ANSI Z83.8-2009/CSA 2.6.-2009. Unit shall be of power vented design. Gravity vented units shall not be acceptable.
6. CAPACITIES AND PERFORMANCE
7. All heaters are to have a minimum thermal efficiency of 83%. Unit performance shall be the sizes, capacities and configurations as scheduled on drawings.
8. UNIT CONSTRUCTION
9. Most cabinetry and trim pieces shall be fabricated of 20-gauge 430 Stainless Steel. Cabinet finish shall be unpainted.
10. Unit shall be insulated with foil faced insulation. Insulation shall have a fire hazard classification of 25/50 Flame Spread/Smoke Developed Rating per ASTM E 84, UL 723 and CAN/UCL S102-M88.
11. All line voltage wiring shall be completely enclosed in flexible conduit.
12. Top panel of unit shall have a minimum of (2) integrated Nutserts for unit suspension with threaded rod.
13. HEAT EXCHANGER AND BURNER
14. The heat exchanger shall consists of 409 stainless steel tubes not lighter than 20-gauge. Tubes shall be of a curved, non-welded serpentine design. Clamshell heat exchangers and welded heat exchangers shall not be acceptable.
15. Burner shall be constructed of aluminized steel. (Optional) Burners shall be constructed of 304L Stainless Steel. Burners shall be of the “in-shot” design.
16. Flue collector shall be constructed of 430 stainless steel.
17. UNIT FAN
18. Unit fan shall be of the propeller type. Propeller blades shall be constructed of aluminum and hubbed to the fan shaft. Fan blade shall be locked into location via set screw.
19. Motor sizes shall be minimum sizes as indicated on schedule. If not indicated, motor size shall be large enough so driven load will not require motor to operate in service factor range above 1.0.
20. Units will be equipped with 115/1/60 volt open drip proof motors which include internal automatic reset thermal overload protection. (Option) Units will be equipped with 115/1/60 volt totally enclosed motors which include internal automatic reset thermal overload protection.
21. For voltages other than 115/1/60, a unit must be supplied with the corresponding field installed transformer to step the voltage down to 115/1/60.
22. All fans shall be provided with manufactures standard fan-blade guard. (Optional) Provide factory installed fan-blade guard, comply with OSHA specifications. Guard must be removable for maintenance.
23. Units with inputs greater than 250,000 BTU’s shall be equipped with dual motors and blades for optimum air distribution.
24. CONTROLS
25. Provided 24 volt, single stage, redundant gas control valve. Valve shall be fast opening type. (Option) Provide 24 volt, two-stage, redundant gas control valve. Valve shall be fast opening type.
26. A direct spark ignition system with integrated control shall be provided. Flame rectification shall be independent of the spark igniter allowing true indication of complete ignition of the burner. Standing pilot shall not be acceptable.
27. Integrated electronic control board shall be used to regulate the system sequence of operation, including an onboard LED indicator for ease of troubleshooting.
28. Control transforms - Heaters shall be equipped with a 120/24 volt transformer. The control transformer and pressure switch shall be factory mounted in a main control panel located on the side of the unit; this panel creates easy access and all wiring information will be indicated on the inside control panel door.
29. The following safeties shall be provided:
    1. High Limit Switch -Units shall be equipped with a low voltage automatic reset high temperature control, wired to de-energize the main gas valve and maintain fan operation until the high temperature control resets.
    2. Air Pressure Switch – Units shall be equipped with an air pressure switch to confirm power venter operation prior to beginning ignition sequence and normal operation.
    3. Flame Sensor – shall monitor ignition and normal operation. If flame is not detected after 3 ignition periods, the control will de-energizes the gas valve and lockout the unit requiring manual reset.
30. Thermostat terminal strip shall be mounted on the exterior of the electrical control panel for ease of installation and wiring.
31. Line voltage wiring will terminate inside electrical cabinet.
32. (Optional) Thermostat – Unit shall be provided with a ship loose thermostat for field install. Thermostats shall be mercury free.
    1. Single stage heating only thermostat shall be provided. Subbase shall include fan switching relay. Temperature range: 50-100°F. range. (Optional) Thermostat shall be standard round style. (Optional) Thermostat shall include tamper proof guard. (Optional) Thermostat shall include tamper proof guard. (Optional) Thermostat supply voltage shall be 120 VAC.
    2. Two Stage Thermostat with subbase shall be provided. Thermostat shall include two stage heating and two stage cooling with system and fan switching and built in 10°F heating/cooling differential. Thermostat shall include fan switching relay. Temperature range: Heating 40-90°F., Cooling 50-99 °F.
33. DISCHARGE LOUVERS:
    1. Louvers shall be individually adjustable and removable with horizontal blades for directing air flow.

1. ACCESSORIES
   1. (Optional) Unit shall be provided with high pressure regulator to reduce supply gas pressure. High pressure regulator will ship loose for field install.
   2. (Optional) Vent cap shall be provided with unit, shipped loose for field install.

**PART 3 – EXECUTION**

1. EXAMINATION
2. Examine area to receive unit heater for compliance with requirements for installation clearances and other conditions affecting unit heater performance. Do not proceed with installation until unsatisfactory conditions have been corrected.
3. INSTALLATION
4. Install unit heater level and plumb, according to manufacturer’s written instructions and referenced standards.

1. Install gas fired unit heater according to NFPA 54, and applicable federal and local code.
2. Support suspended unit heater per manufactures instructions.
3. Install electrical devices furnished with unit heater, but not specified to be factory mounted.
4. CONNECTIONS
5. All gas piping should be sized in accordance with the latest edition of ANSI Standard Z223.1, National Fuel Gas Code; in Canada, according to CSA B149.

1. If supply gas pressure exceeds 14 inches W.C. a high pressure regulating valve must be installed in the line upstream from the main shut off valve.
2. Connect gas piping to unit heater gas train inlet with ground joint union. A manual shut off valve (field provided) should be field install immediately upstream of the gas supply connection to the unit heater.
3. Piping must be adequately supported to prevent strain on the gas manifold and controls.
4. To prevent the mixing of moisture with the gas, run the take-off piping from the top or side of the main gas line.
5. Provide a drip leg in the gas piping near the unit heater.
6. Make certain that all connections have been adequately doped and tightened.
7. Electrical: Comply with applicable requirements in Division 26 Sections.
8. All external wiring must conform to the latest edition of ANSI/NFPA No. 70, United States National Electrical Code, and applicable local codes; in Canada, to the Canadian Electrical Code, Part 1, CSA Standard C22.1
9. A disconnect switch (field provided) of suitable electrical rating should be located as close to the gas valve and controls as possible.
10. Each unit heater must be electrically grounded in accordance with the latest edition of ANSI/NFPA No. 70, United States National Electrical Code, and applicable local codes; in Canada, to the Canadian Electrical Code, Part 1, CSA Standard C22.1.
11. Thermostat must be mounted on a vertical, vibration free surface, free from air currents and in accordance with the furnished instruction.
12. Thermostat shall be mounted at a height of approximately 5 feet above the floor, in an area where it will be exposed to a free circulation of average temperature air.
13. Venting: All venting installations shall be in accordance with the latest edition of ANSI Z223.1, Part 7, Venting of Equipment of the National Fuel Gas Code or applicable provisions of local building codes.
14. Pipe exhaust venting per manufactures instructions.
15. Venting must be sloped to prevent any condensate from draining into the unit heater.
16. CLEANING
17. Gas line must be purged prior to startup of unit heater.
18. Unit should be cleaned of all construction debris and any dust that may have accumulated on interior of unit, burner or any part of the heat exchanger.
19. All vent piping must be free of any blockage that may affect airflow.
20. FIELD QUALITY CONTROL
21. Manufacturer’s Field Service: Engage a factory authorized service representative to inspect the field assembled components and installation of unit heater, including piping and electrical connections. Report results in writing.
    * 1. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.
22. Manufacturer’s representative shall supply a factory authorized service technician to start up the unit heater.
23. COMMISSIONING
24. Engage a factory authorized service representative to provide startup service. Start up to be performed only after space is field verified to offer a substantial load.
25. Verify that installation is as indicated and specified.
26. Verify that electrical wiring installation complies with manufacturer’s submittal and installation instructions as well as any requirements in Division 26 Sections. Do not proceed with unit heater startup until wiring installation is acceptable to equipment Installer.
27. Complete manufacturer’s installation and startup checklist and verify the following:
28. Unit heater is installed level and incompliance with manufacture’s instruction.
29. Vent piping is sized correctly and installed without visible damage.
30. No damage is visible to unit heater cabinet, heat exchanger, or fan assembly. Fan should rotate freely.
31. Gas piping and electric wiring have been installed properly and inspected by the local authority having jurisdiction.
32. Supply gas pressure is within manufactures requirements.
33. Clearances have been provided and piping is correct per all applicable codes.
34. A field installed controls have been installed and operational.
35. Labels are clearly visible.
36. Unit heater, burner, and flue are clean and free of construction debris.
37. Perform the following tests for high fire rating for burners. Adjust unit heater combustion efficiency at given firing rate. Measure and record the following:
38. Supply voltage.
39. Motor amps.
40. Inlet gas pressure. If multiple units are connected to the same inlet gas line, measure inlet gas pressure when all valves on the line are full open.
41. Gas pressure on manifold. Manifold pressure should be set to 3.5 inches W.C for natural gas and 10.0 inches of W.C. for propane gas.
42. Cycle on high limit.
43. Combustion analysis, Carbon Monoxide (PPM). Caron Dioxide or O2 (%).
44. Measure and record temperature rise through each unit heater.
45. MAINTENANCE
46. For units used during the construction phase of the project, installing contractor shall be responsible for all maintenance associated with running the unit. Maintenance shall be performed per the manufacturer’s instructions at the manufacturer’s required intervals.
47. DEMONSTRATION
48. Engage a factory authorized service representative to train Owner’s maintenance personnel as

specified below:

1. Operate unit heater, including accessories and controls, to demonstrate compliance with requirements.
2. Train Owner’s maintenance personnel on procedures and schedules related to startup and shutdown, troubleshooting, servicing, and preventive maintenance.
3. Review data in the maintenance manuals. Refer to Division 1 Section “Contract Closeout.”
4. Review data in the maintenance manuals. Refer to Division 1 Section “Operation and Maintenance Data.”
5. Schedule training with Owner with at least 7 days advance notice.

END OF SECTION