Section 23 55 33.16 – *Sample Specification for Sterling QVED/QVES Gas Fired Unit Heaters*

**PART 1 – GENERAL**

* 1. RELATED DOCUMENTS

1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.
   1. SUMMARY
2. This section includes gas-fired unit heaters
   1. INFORMATIONAL SUBMITTALS
3. Product Data: For each type of gas-fired unit heater indicated. Include rated capacities, operating characteristics, and accessories.
4. Shop Drawings: For gas-fired unit heaters.
   1. Detail equipment assemblies and indicate dimensions, weights, required clearances, components, and location and size of each field connection
   2. Wiring Diagrams: Power and control wiring.
   3. MAINTENANCE MATERIAL SUBMITTALS
5. Operation and Maintenance Data: For gas-fired unit heaters to include, installation, operation, and maintenance manuals.
   1. QUALITY ASSURANCE
6. Equipment, Electrical Components, Devices, and Accessories: Listed and labeled as defined by Intertek’s ETL certification.
7. Comply with the following codes and standards where applicable:
8. ANSI Z83.8 -2009/CSA 2.6-2009 – American National Standard/CSA Standard for Gas Unit Heaters, Gas Packaged Heaters, Gas Utility Heaters and Gas-Fired Duct Furnaces.
9. ASHRAE/IESNA 90.1-2010 – Applicable requirements in ASHRAE/IESNA 90.1-2010, Section 6 – “Heating, Ventilating, and Air-Conditioning”.
10. NFPA 70, National Electric Code for electrical components and installation.
11. NFPA 54, National Fuel Code for gas components and installation.
    1. WARRANTY
12. Special Warranty: Manufacturer’s standard form in which manufacturer agrees to repair or replace components listed below of gas-fired unit heater that fails in materials or workmanship within the specified warranty period.
13. Warranty Period for Heat Exchangers: Manufacturer’s standard, but not less than 1 years from the date of shipment. Warranty shall be non-prorated.

**PART -2 – PRODUCTS**

1. MANUFACTURES
2. Available Manufacturers: Subject to compliance with requirements, provide products by one of the following or approved equal:
   1. Sterling HVAC Products
   2. (The) Trane Company
   3. Beacon Morris Heating Products
3. Manufacture must have a minimum of 5 year experience manufacturing the products specified in this section.
4. GENERAL
5. Furnish and install, where indicated or scheduled on plans, gas-fired unit heaters. Unit shall be factory assembled, piped and wired, and complying with ANSI Z83.8-2009/CSA 2.6.-2009. Unit shall be of power vented design. Gravity vented units shall not be acceptable.
6. CAPACITIES AND PERFORMANCE
7. All heaters are to have a minimum thermal efficiency of 80%. Unit performance shall be the sizes, capacities and configurations as scheduled on drawings.
8. UNIT CONSTRUCTION
9. Most cabinetry and trim pieces shall be fabricated of 20-gauge material and painted with a baked gray enamel finish.
10. All line voltage wiring shall be completely enclosed in flexible conduit.
11. Unit heater shall have a minimum of (4) built in hanger brackets for suspension of unit.
12. HEAT EXCHANGER AND BURNER
13. The heat exchanger shall be constructed of aluminized steel not lighter than 20-gauge with 18-gauge headers. (Optional) The heat exchanger shall be constructed of 409 Stainless steel not lighter than 20-gauge with 18-gauge headers. (Optional) The heat exchanger shall be constructed of 321 Stainless steel not lighter than 20-gauge with 18-gauge headers.
14. Burner shall be constructed of aluminized steel. (Optional) Burners shall be constructed of 409 Stainless Steel. Burners shall be equipped with burner shade/V Port to minimize scale of foreign matter and for ease of cleaning.
15. Flue Collector shall be construction of aluminized steel. (Optional) Flue Collector shall be constructed of 409 Stainless Steel.
16. Unit shall have bottom access for service the burner (QVED). Unit shall have side access for burner service (QVES)
17. (Optional) 409 Stainless Steel Drip Pan shall be shipped loose for field install underneath the burner section.
18. CONTROLS
19. The following gas control shall be provided with the unit.
    1. (Standard) Provided 24 volt, single stage, redundant gas control valve. Valve shall be fast opening type.
    2. (Option) Provide 24 volt, two-stage, redundant gas control valve. Valve shall be fast opening type.
    3. (Option) Unit shall be provided with electronic modulating gas valve. Gas valve shall be capable of modulating from 100% to 40% of full fire rate. An automatic valve in series with the modulating valve will be provided to cycle the unit. Automatic valve shall be of the fail closed type to prevent the flow of gas in the event of a power failure.
       1. (Optional) Modulating gas valve shall be controlled via 4-20mA or 0-10VDC signal from the Building Automation System.
       2. (Optional) Valve modulation shall be controlled via a room sensor to maintain room temperature. Unit shall be capable of maintaining a constant discharge temperature within ±1°F.
       3. (Optional) Valve modulation shall be controlled via a duct sensor to maintain a constant discharge temperature within ±1°F.
       4. (Optional) Valve modulation shall be controlled via a duct sensor to maintain a constant discharge temperature within ±1°F. A room override stat will provided to override modulation and allow 100% fire when the room temperature drops below room set point.
20. A Solid State spark ignition system shall be provided. Spark shall ignite the pilot burner. When pilot flame is proven, main burner valve will open. If burner fails to light after 90 seconds then the control will go into 5 minute delay ignition will restart ignition sequence. (Option) If pilot fails to light, pilot gas and spark shall go to off position (100% shutoff), and lockout.
21. Control transforms - Heaters shall be equipped with a 120/24 volt transformer.
22. The following safeties shall be provided:
    1. High Limit Switch -Units shall be equipped with a low voltage automatic reset high temperature control, wired to de-energize the main gas valve until the high temperature control resets.
    2. (Optional) Adjustable High Limit Switch shall be installed in series with safety high limit. Adjustable high limit shall allow the user to set a temperature limit below factory safety limit and shall not override the safety high limit switch.
    3. (Optional) Air Pressure Switch – Units shall be equipped with an air pressure switch to confirm power venter operation prior to beginning ignition sequence.
    4. (Optional) Adjustable Fan Switch – Unit shall be equipped with an adjustable fan switch for control of a separate blower. When the temperature drops below the set point, the switch shall disengage the blower until the temperature rises above set point.
    5. Pilot Flame Sensor – If the pilot fails to light, the control module will not energize the second (main) gas valve and the main burner will not light. After 5 minutes, the control module restarts the ignition sequence. (Optional) If flame is not detected after 90 seconds, the control will de-energizes the gas valve and lockout the unit requiring manual reset.
    6. (Optional) Fan Time Delay shall be provided factory installed on the unit. Time delay will provide a 60 delay on a call for heat and 45 second delay on off for blower operation.
23. (Optional) Thermostat – Unit shall be provided with a ship loose thermostat for field install. Thermostats shall be mercury free.
    1. Single stage heating only thermostat shall be provided. Subbase shall include fan switching relay. Temperature range: 50-100°F. range. (Optional) Thermostat shall be standard round style. (Optional) Thermostat shall include tamper proof guard. (Optional) Thermostat shall include tamper proof guard. (Optional) Thermostat supply voltage shall be 120 VAC.
    2. Two Stage Thermostat with subbase shall be provided. Thermostat shall include two stage heating and two stage cooling with system and fan switching and built in 10°F heating/cooling differential. Thermostat shall include fan switching relay. Temperature range: Heating 40-90°F., Cooling 50-99 °F.
    3. (Optional) One Stage Duct Thermostat shall be provided. Thermostat shall be single pole double throw switching. Temperature range: 55-175°F.
    4. (Optional) Two Stage Duct Thermostat shall be provided. Thermostat shall be single pole double throw switching. Temperature range: 55-175°F.
24. (Option) Low ambient control shall be provided to disengage propeller motor when the temperature drops below the set point. Upon a rise in ambient temperature above the set point, the control turns the fan back on and allows normal operation. Control shall be provide ship loose for field wiring to the blower motor provided by others
25. (Optional) Summer/Winter Switch shall be provided by unit manufacture. Switch shall permit the use of blower for continuous air circulation when combined with thermostat with built in fan switch.
26. (Optional) Thermostat Terminal Block shall be factory installed for ease of field wiring.
27. DISCHARGE LOUVERS (OPTIONAL):
    1. (Optional) Horizontal and vertical louvers shall also be provided to allow for the 4 way air deflection. Louvers shall be individually adjustable and removable for directing air flow.
28. ACCESSORIES
29. (Optional) Unit shall be provided with high pressure regulator to reduce supply gas pressure. High pressure regulator will ship loose for field install.
30. (Optional) Vent cap shall be provided with unit, shipped loose for field install.

**PART 3 – EXECUTION**

1. EXAMINATION
2. Examine area to receive unit heater for compliance with requirements for installation clearances and other conditions affecting unit heater performance. Do not proceed with installation until unsatisfactory conditions have been corrected.
3. INSTALLATION
4. Install unit heater level and plumb, according to manufacturer’s written instructions and referenced standards.

1. Install gas fired unit heater according to NFPA 54, and applicable federal and local code.
2. Support suspended unit heater per manufactures instructions.
3. Install electrical devices furnished with unit heater, but not specified to be factory mounted.

1. CONNECTIONS
2. All gas piping should be sized in accordance with the latest edition of ANSI Standard Z223.1, National Fuel Gas Code; in Canada, according to CSA B149.

1. If supply gas pressure exceeds 14 inches W.C. a high pressure regulating valve must be installed in the line upstream from the main shut off valve.
2. Connect gas piping to unit heater gas train inlet with ground joint union (field provided). A manual shut off valve (field provided) should be field install immediately upstream of the gas supply connection to the unit heater.
3. Piping must be adequately supported to prevent strain on the gas manifold and controls.
4. To prevent the mixing of moisture with the gas, run the take-off piping from the top or side of the main gas line.
5. Provide a drip leg in the gas piping near the unit heater.
6. Make certain that all connections have been adequately doped and tightened.
7. Electrical: Comply with applicable requirements in Division 26 Sections.
8. All external wiring must conform to the latest edition of ANSI/NFPA No. 70, United States National Electrical Code, and applicable local codes; in Canada, to the Canadian Electrical Code, Part 1, CSA Standard C22.1
9. A disconnect switch (field provided) of suitable electrical rating should be located as close to the gas valve and controls as possible.
10. Each unit heater must be electrically grounded in accordance with the latest edition of ANSI/NFPA No. 70, United States National Electrical Code, and applicable local codes; in Canada, to the Canadian Electrical Code, Part 1, CSA Standard C22.1.
11. Thermostat must be mounted on a vertical, vibration free surface, free from air currents and in accordance with the furnished instruction.
12. Thermostat shall be mounted at a height of approximately 5 feet above the floor, in an area where it will be exposed to a free circulation of average temperature air.
13. Venting: All venting installations shall be in accordance with the latest edition of ANSI Z223.1, Part 7, Venting of Equipment of the National Fuel Gas Code or applicable provisions of local building codes.
14. Pipe exhaust venting per manufactures instructions.
15. Venting must be sloped to prevent any condensate from draining into the unit heater..
16. Ductwork: Duct connection flanges and seams must be sealed to prevent air leaks. Sealant/tape must be suitable for a minimum temperature of 250 °F. All ductwork must be installed per local code and regulation and manufactures instructions. See installation, operation, and maintenance manuals for additional instructions.
17. CLEANING
18. Gas line should be purged prior to startup of unit heater.
19. Unit should be cleaned of all construction debris and any dust that may have accumulated on interior of unit, burner or any part of the heat exchanger.
20. All vent piping must be free of any blockage that may affect airflow.
21. FIELD QUALITY CONTROL
22. Manufacturer’s Field Service: Engage a factory authorized service representative to inspect the field assembled components and installation of unit heater, including piping and electrical connections. Report results in writing.
    * 1. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.
23. Manufacturer’s representative shall supply a factory authorized service technician to start up the unit heater.
24. COMMISSIONING
25. Engage a factory authorized service representative to provide startup service. Start up to be performed only after space is field verified to offer a substantial load.
26. Verify that installation is as indicated and specified.
27. Verify that electrical wiring installation complies with manufacturer’s submittal and installation instructions as well as any requirements in Division 26 Sections. Do not proceed with unit heater startup until wiring installation is acceptable to equipment Installer.
28. Complete manufacturer’s installation and startup checklist and verify the following:
29. Unit heater is installed level and incompliance with manufacture’s instruction.
30. Vent piping is sized correctly and installed without visible damage.
31. No damage is visible to unit heater cabinet or heat exchanger
32. Gas piping and electric wiring have been installed properly and inspected by the local authority having jurisdiction.
33. Supply gas pressure is within manufactures requirements.
34. Clearances have been provided and piping is correct per all applicable codes.
35. A field installed controls have been installed and operational.
36. Labels are clearly visible.
37. Unit heater, burner, and flue are clean and free of construction debris.
38. Perform the following tests for high fire rating for burners. Adjust unit heater combustion efficiency at given firing rate. Measure and record the following:
39. Supply voltage.
40. Inlet gas pressure. If multiple units are connected to the same inlet gas line, measure inlet gas pressure when all valves on the line are full open.
41. Gas pressure on manifold. Manifold pressure should be set to 3.5 inches W.C for natural gas and 10.0 inches of W.C. for propane gas.
42. Cycle on high limit.
43. Combustion analysis, Carbon Monoxide (PPM). Caron Dioxide or O2 (%)
44. Measure and record temperature rise through each unit heater.
45. MAINTENANCE
46. For units used during the construction phase of the project, installing contractor shall be responsible for all maintenance associated with running the unit. Maintenance shall be performed per the manufacturer’s instructions at the manufacturer’s required intervals.
47. DEMONSTRATION
48. Engage a factory authorized service representative to train Owner’s maintenance personnel as

specified below:

1. Operate unit heater, including accessories and controls, to demonstrate compliance with requirements.
2. Train Owner’s maintenance personnel on procedures and schedules related to startup and shutdown, troubleshooting, servicing, and preventive maintenance.
3. Review data in the maintenance manuals. Refer to Division 1 Section “Contract Closeout.”
4. Review data in the maintenance manuals. Refer to Division 1 Section “Operation and Maintenance Data.”
5. Schedule training with Owner with at least 7 days advance notice.

END OF SECTION