RSD SERIES

ARCHITECTURAL/ENGINEERING SHORT FORM SPECIFICATIONS

Gas-fired infrared space heaters shall be furnished and installed in accordance with governing codes and as shown per building drawing(s) as described below:

Heaters shall be Sterling RSD series ceramic heaters, model number RSD_________, rated at _____________ Btu/hr.  Heaters shall be equipped with a 24-volt direct spark ignition system with 100% gas shutoff and redundant combination gas valve.

Heaters shall be made of aluminized steel body construction and shall consist of multiple burner heads. Heaters shall utilize special honeycomb tile design for increased radiant output.  Heaters shall utilize aluminum reflectors with reflectivity rating of 97.5%

As an option, heaters may be equipped with an Incoloy 800 reverberatory screen.  The reverberatory screen will increase the overall emissivity of the radiant surface with a blackbody radiation effect and will act as a protective safety screen in the unlikely event that the ceramic tile assembly is broken by an outside force.  The heater's tile temperature can vary from 1650ºF to 1800ºF and the tiles shall withstand thermal shock when water quenched.

Heaters shall operate satisfactorily in any position from horizontal to thirty-five (35º) degrees from horizontal.  Heaters shall be design certified by C.S.A. to American National Standard Z83.19-latest edition/CSA Standard 2.35-latest edition.  The manufacturer shall provide a written limited warranty of one (1) year  covering the emitter tiles and a limited warranty of one (1) year for all components utilized in the heater's control assembly.

SpecRSD Rev. A

Nov-01