## HiddenTables (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39
EAT/EWT Correction factor for BTU
This table applies to Cabinet Unit Heaters
| sheetname | HiddenTables
| FindVertValue |  | EAT |  | Source: Vulcan Cabinet Unit Heater Catalog 415.10 page 12
| findHorizValue |  | EWT
| SeachCol | 6 | EAT
| SearchRow | 15 | EWT |  |  | ENTERING WATER TEMP - 20 DEG TEMP DROP
| FirstRow | 16 |  |  | EAT | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300
| LastRow | 23 |  |  | 30 | 0.518 | 0.666 | 0.814 | 0.963 | 1.12 | 1.26 | 1.408 | 1.555 | 1.702 | 1.85 | 1.997
| FirstCol | 7 |  |  | 40 | 0.439 | 0.585 | 0.731 | 0.878 | 1.025 | 1.172 | 1.317 | 1.464 | 1.609 | 1.755 | 1.908
| LastCol | 17 |  |  | 50 | 0.361 | 0.506 | 0.651 | 0.796 | 0.941 | 1.085 | 1.231 | 1.375 | 1.518 | 1.663 | 1.824
| Result | 1 | Corr Fac |  | 60 | 0.286 | 0.429 | 0.571 | 0.715 | 0.857 | 1 | 1.143 | 1.286 | 1.429 | 1.571 | 1.717
[5 empty] | 70 | 0.212 | 0.353 | 0.494 | 0.636 | 0.777 | 0.918 | 1.06 | 1.201 | 1.342 | 1.483 | 1.63
[5 empty] | 80 | 0.14 | 0.279 | 0.419 | 0.558 | 0.698 | 0.837 | 0.977 | 1.117 | 1.257 | 1.397 | 1.545
[5 empty] | 90 | 0.11836 | 0.279 | 0.35424 | 0.483 | 0.621 | 0.759 | 0.897 | 1.035 | 1.173 | 1.311 | 1.462
[5 empty] | 100 | 0 | 0.137 | 0.273 | 0.409 | 0.546 | 0.682 | 0.818 | 0.955 | 1.094 | 1.23 | 1.371
[6 empty] | EAT | 70
|  |  |  | delete????? |  | CF | 0.96488 |  | <-- doesn't work well above 60 deg eat
Correction Factors for Water Temp. Drop
correction factors taken from Vulcan Cabinet Unit Heaters Catalog 415.10 page 12
| sheetname | HiddenTables
| searchcol | 6 |  |  | WTD | GPM | BTU | WPD
| GPMCol | 7 |  |  | 5 | 5 | 1.25 | 10
| BTUCol | 8 |  |  | 10 | 2.3 | 1.15 | 5
| WPDCol | 9 |  |  | 15 | 1.44 | 1.08 | 2
| FirstRow | 39 |  |  | 20 | 1 | 1 | 1
| LastRow | 47 |  |  | 25 | 0.74 | 0.94 | 0.6
| result | 1 | GPM |  | 30 | 0.59 | 0.9 | 0.4
| result | 1 | BTU |  | 40 | 0.4 | 0.83 | 0.2
| result | 1 | WPD |  | 50 | 0.3 | 0.76 | 0.13
[5 empty] | 60 | 0.24 | 0.72 | 0.07
External Static Pressure Correction factor for BTU
| sheetname | HiddenTables |  |  | This table applies to Cabinet Unit Heaters
| FindValue |  | ESP
| SeachCol | 6 | ESP |  | ESP | CF
| FirstRow | 61 |  |  | 0 | 1
| LastRow | 64 |  |  | 0.05 | 0.92
| DataCol | 7 |  |  | 0.1 | 0.82
| Result | 1 | Corr Fac |  | 0.125 | 0.79
Altitude Correction factor for BTU
[5 empty] | This table is air density ratio | [6 empty] | This table applies to cabinet and regular unit heaters
Pervious lookup table
[5 empty] | Per calculations by M. Girard March 2014 | [6 empty] | Table from ASHREA High Altitude Effects Symposium 1965 figure 4, page 48
| sheetname | HiddenTables |  |  | Altitude | cf | [5 empty] | Altitude | cf
| FindValue |  | Altitude |  | 0 | 1 | [5 empty] | 0 | 1
| SeachCol | 6 | Altitude |  | 1000 | 0.97094 | [5 empty] | 1000 | 0.975
| FirstRow | 79 |  |  | 2000 | 0.94252 | [5 empty] | 2000 | 0.95
| LastRow | 88 |  |  | 3000 | 0.91475 | [5 empty] | 3000 | 0.925
| DataCol | 7 |  |  | 4000 | 0.88761 | [5 empty] | 4000 | 0.905
| Result | 0.99935 | Corr Fac |  | 5000 | 0.86109 | [5 empty] | 5000 | 0.88
[5 empty] | 6000 | 0.83518 | [5 empty] | 6000 | 0.86
[5 empty] | 7000 | 0.80987 | [5 empty] | 7000 | 0.84
[5 empty] | 8000 | 0.78515 | [5 empty] | 8000 | 0.82
[5 empty] | 9000 | 0.76102 | [5 empty] | 9000 | 0.8
[5 empty] | 10000 | 0.73745 | [5 empty] | 10000 | 0.78
PSI Correction factor for BTU
[5 empty] | This table applies to Cabinet Unit Heaters | [7 empty] | See Water sheet for Finned tube factors
[5 empty] | Source: Nesbitt Propeller Fan Unit Heater Catalog and |  |  |  |  | Vulcan Cabinet Unit Heater Catalog 415.10 page 12
| sheetname | HiddenTables |  |  |  | Steam Pressure PSI
| FindVertValue |  | EAT |  | EAT | 0 | 2 | 5 | 10 | 15 | 20 | 30 | 40 | 50 | 60 | 70 | 75 | 80 | 90 | 100 | 125 | 150
| findHorizValue |  | PSI |  | -10 | 1.54 | 1.585 | 1.64 | 1.73 | 1.799 | 1.861 | 1.966 | 2.058 | 2.134 | 2.196 | 2.256 | 2.283 | 2.312 | 2.361 | 2.409 | 2.52 | 2.605
| SeachCol | 6 | EAT |  | 0 | 1.45 | 1.495 | 1.55 | 1.639 | 1.708 | 1.769 | 1.871 | 1.959 | 2.035 | 2.094 | 2.157 | 2.183 | 2.211 | 2.258 | 2.307 | 2.42 | 2.5
| SearchRow | 103 | PSI |  | 10 | 1.37 | 1.405 | 1.456 | 1.545 | 1.614 | 1.675 | 1.775 | 1.862 | 1.936 | 1.997 | 2.057 | 2.085 | 2.112 | 2.159 | 2.204 | 2.31 | 2.394
| FirstRow | 108 |  |  | 20 | 1.27 | 1.32 | 1.37 | 1.46 | 1.525 | 1.584 | 1.684 | 1.771 | 1.845 | 1.902 | 1.961 | 1.99 | 2.015 | 2.063 | 2.108 | 2.205 | 2.315
| LastRow | 115 |  |  | 30 | 1.19 | 1.24 | 1.29 | 1.38 | 1.44 | 1.5 | 1.6 | 1.68 | 1.76 | 1.811 | 1.872 | 1.896 | 1.925 | 1.968 | 2.015 | 2.115 | 2.221
| FirstCol | 7 |  |  | 40 | 1.11 | 1.16 | 1.21 | 1.29 | 1.34 | 1.42 | 1.51 | 1.6 | 1.67 | 1.725 | 1.782 | 1.808 | 1.836 | 1.88 | 1.927 | 2.022 | 2.105
| LastCol | 23 |  |  | 50 | 1.03 | 1.08 | 1.13 | 1.21 | 1.28 | 1.33 | 1.43 | 1.51 | 1.58 | 1.64 | 1.696 | 1.721 | 1.748 | 1.792 | 1.836 | 1.94 | 2.015
| Result | 1.0253 | Corr Fac |  | 60 | 0.96 | 1 | 1.05 | 1.13 | 1.19 | 1.25 | 1.35 | 1.43 | 1.5 | 1.555 | 1.61 | 1.635 | 1.66 | 1.705 | 1.749 | 1.845 | 1.925
[5 empty] | 70 | 0.88 | 0.93 | 0.97 | 1.06 | 1.12 | 1.17 | 1.27 | 1.35 | 1.42 | 1.472 | 1.527 | 1.552 | 1.577 | 1.621 | 1.663 | 1.76 | 1.837
[5 empty] | 80 | 0.81 | 0.85 | 0.9 | 0.98 | 1.04 | 1.1 | 1.19 | 1.27 | 1.34 | 1.393 | 1.447 | 1.472 | 1.497 | 1.541 | 1.581 | 1.675 | 1.755
[5 empty] | 90 | 0.74 | 0.78 | 0.83 | 0.91 | 0.97 | 1.02 | 1.12 | 1.19 | 1.26 | 1.314 | 1.368 | 1.392 | 1.418 | 1.461 | 1.502 | 1.6 | 1.672
[5 empty] | 100 | 0.67 | 0.71 | 0.76 | 0.84 | 0.9 | 0.95 | 1.04 | 1.12 | 1.19 | 1.239 | 1.293 | 1.316 | 1.342 | 1.383 | 1.424 | 1.514 | 1.592
CFM Correction factor for Entering Air Temperature (EAT)
From Nesbitt Propeller Fan Unit Heater Catalog, Publication 41-1
| sheetname | HiddenTables |  |  | EAT | Corr. Fac.
| FindValue |  | EAT |  | -10 | 1.155
| SeachCol | 6 | EAT |  | 0 | 1.13
| FirstRow | 135 |  |  | 10 | 1.105
| LastRow | 142 |  |  | 20 | 1.082
| DataCol | 7 |  |  | 30 | 1.06
| Result | 1 | Corr Fac |  | 40 | 1.04
[5 empty] | 50 | 1.02
[5 empty] | 60 | 1
[5 empty] | 70 | 0.982
[5 empty] | 80 | 0.964
[5 empty] | 90 | 0.945
[5 empty] | 100 | 0.93
Latent Heat of Steam For Condensate Calculation
From Vulcan Cabinet Unit Heater Catalog 415.10 page 11
| sheetname | HiddenTables |  |  | psi | latent heat
| FindValue |  | PSI |  | 0 | 970
| SeachCol | 6 | PSI |  | 2 | 966.3
| FirstRow | 157 |  |  | 5 | 960.7
| LastRow | 173 |  |  | 10 | 952.4
| DataCol | 7 |  |  | 15 | 945.5
| Result | 965.9723 | Latent Heat |  | 20 | 939.3
[5 empty] | 30 | 928.5
[5 empty] | 40 | 918.3
[5 empty] | 50 | 911.2
[5 empty] | 60 | 903.9
[5 empty] | 70 | 897.3
[5 empty] | 75 | 893.8
[5 empty] | 80 | 891.1
[5 empty] | 90 | 885.4
[5 empty] | 100 | 880
[5 empty] | 125 | 867.8
[5 empty] | 150 | 856.9
Static Pressure Correction Factor for CFM
This table applies to Cabinet Unit Heaters
| sheetname | HiddenTables
| FindValue |  | PSI |  |  | CFM | CF | CFM | CF | CFM | CF | CFM | CF | CFM | CF | CFM | CF | CFM | CF | CFM | CF
| SeachCol | 6 | PSI |  | ESP | size 02 |  | size 03 |  | size 04 |  | size 06 |  | size 08 |  | size 10 |  | size 12 |  | size 14
| FirstRow | 188 |  |  | 0 | 230 | 1 | 335 | 1 | 430 | 1 | 630 | 1 | 860 | 1 | 1060 | 1 | 1230 | 1 | 1410 | 1
| LastRow | 191 |  |  | 0.05 | 205 | 0.8913 | 290 | 0.86567 | 390 | 0.90698 | 560 | 0.88889 | 750 | 0.87209 | 925 | 0.87264 | 1060 | 0.86179 | 1210 | 0.85816
| DataCol | 8 |  |  | 0.1 | 165 | 0.71739 | 240 | 0.71642 | 315 | 0.73256 | 450 | 0.71429 | 620 | 0.72093 | 755 | 0.71226 | 865 | 0.70325 | 980 | 0.69504
| Result | 1 | Corr factor |  | 0.125 | 145 | 0.63043 | 210 | 0.62687 | 275 | 0.63953 | 400 | 0.63492 | 540 | 0.62791 | 660 | 0.62264 | 750 | 0.60976 | 850 | 0.60284
| sheetname | HiddenTables |  |  | Ethylene Glycol Correction factor for BTU
| FindVertValue |  | temp
| findHorizValue |  | percent
| SeachCol | 6 | temp |  | This table applies to All products, based on fig 10 curves from ASHRAE Fundementals pg 18.10
| SearchRow | 206 | percent
| FirstRow | 213 |  |  |  | Percent Glycol
| LastRow | 223 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90
| FirstCol | 7 |  |  | Fluid | Specific heat | Specific heat | Specific heat | Specific heat | Specific heat | Specific heat | Specific heat | Specific heat | Specific heat
| LastCol | 15 |  |  | Temp | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg
| Result | 0.946 | Corr Fac |  | -30 | Percent Glycol 50: 0.74; Percent Glycol 60: 0.68; Percent Glycol 70: 0.63; Percent Glycol 80: 0.57
[5 empty] | -25 | Percent Glycol 50: 0.74; Percent Glycol 60: 0.68; Percent Glycol 70: 0.63; Percent Glycol 80: 0.57
[5 empty] | 0 |  |  |  | 0.8 | 0.75 | 0.7 | 0.64 | 0.59 | 0.53
[5 empty] | 25 |  | 0.9 | 0.86 | 0.81 | 0.77 | 0.72 | 0.66 | 0.61 | 0.55
[5 empty] | 50 | 0.94 | 0.91 | 0.87 | 0.82 | 0.78 | 0.73 | 0.68 | 0.63 | 0.57
[5 empty] | 75 | 0.95 | 0.92 | 0.88 | 0.83 | 0.79 | 0.74 | 0.69 | 0.64 | 0.59
[5 empty] | 100 | 0.96 | 0.92 | 0.88 | 0.84 | 0.8 | 0.76 | 0.71 | 0.66 | 0.61
[5 empty] | 125 | 0.96 | 0.93 | 0.89 | 0.86 | 0.81 | 0.77 | 0.72 | 0.68 | 0.63
[5 empty] | 150 | 0.97 | 0.94 | 0.9 | 0.87 | 0.83 | 0.79 | 0.74 | 0.69 | 0.65
[5 empty] | 175 | 0.97 | 0.94 | 0.91 | 0.88 | 0.84 | 0.8 | 0.76 | 0.71 | 0.67
[5 empty] | 200 | 0.98 | 0.95 | 0.92 | 0.89 | 0.85 | 0.81 | 0.77 | 0.73 | 0.68
[5 empty] | 225 | 0.98 | 0.96 | 0.93 | 0.9 | 0.86 | 0.83 | 0.79 | 0.75 | 0.7
[5 empty] | 250 | 0.99 | 0.97 | 0.94 | 0.91 | 0.87 | 0.84 | 0.81 | 0.76 | 0.72
[5 empty] | 275 | 0.995 | 0.9758 | 0.95 | 0.92 | 0.88 | 0.8508 | 0.8258 | 0.7792 | 0.7358
[5 empty] | 300 | 1 | 0.9833 | 0.96 | 0.93 | 0.89 | 0.8633 | 0.8433 | 0.7967 | 0.7533
| sheetname | HiddenTables |  |  | Propylene Glycol Correction factor for BTU
| FindVertValue |  | temp
| findHorizValue |  | percent
| SeachCol | 6 | temp |  | This table applies to All products, based on fig 14 curves from ASHRAE Fundementals pg 18.10
| SearchRow | 236 | percent
| FirstRow | 242 |  |  |  | Percent Glycol 10: Percent Glycol
| LastRow | 253 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90
| FirstCol | 7 |  |  | Fluid | Specific heat | Specific heat | Specific heat | Specific heat | Specific heat | Specific heat | Specific heat | Specific heat | Specific heat
| LastCol | 15 |  |  | Temp | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg | BTU/lb deg
| Result | 0.986 | Corr Fac |  | -30 | Percent Glycol 50: 0.8; Percent Glycol 60: 0.74; Percent Glycol 70: 0.68; Percent Glycol 80: 0.62; Percent Glycol 90: 0.55
[5 empty] | -25 | Percent Glycol 50: 0.8; Percent Glycol 60: 0.74; Percent Glycol 70: 0.68; Percent Glycol 80: 0.62; Percent Glycol 90: 0.55
[5 empty] | 0 |  |  |  | 0.85 | 0.81 | 0.76 | 0.7 | 0.64 | 0.57
[5 empty] | 25 | 0.96 | 0.94 | 0.9 | 0.87 | 0.83 | 0.77 | 0.72 | 0.65 | 0.59
[5 empty] | 50 | 0.97 | 0.94 | 0.91 | 0.88 | 0.84 | 0.79 | 0.73 | 0.67 | 0.61
[5 empty] | 75 | 0.97 | 0.95 | 0.92 | 0.89 | 0.85 | 0.8 | 0.75 | 0.69 | 0.63
[5 empty] | 100 | 0.98 | 0.96 | 0.93 | 0.9 | 0.86 | 0.82 | 0.77 | 0.71 | 0.65
[5 empty] | 125 | 0.98 | 0.97 | 0.94 | 0.91 | 0.87 | 0.83 | 0.78 | 0.73 | 0.67
[5 empty] | 150 | 0.99 | 0.97 | 0.95 | 0.92 | 0.89 | 0.85 | 0.8 | 0.75 | 0.69
[5 empty] | 175 | 1 | 0.98 | 0.96 | 0.93 | 0.9 | 0.86 | 0.82 | 0.77 | 0.71
[5 empty] | 200 | 1 | 0.99 | 0.97 | 0.94 | 0.91 | 0.87 | 0.83 | 0.78 | 0.73
[5 empty] | 225 | 1.01 | 1 | 0.98 | 0.95 | 0.93 | 0.89 | 0.85 | 0.8 | 0.75
[5 empty] | 250 | 1.01 | 1 | 0.98 | 0.96 | 0.94 | 0.9 | 0.86 | 0.82 | 0.77
[5 empty] | 275 | 1.015 | 1.0092 | 0.9892 | 0.97 | 0.9508 | 0.9108 | 0.8358 | 0.8358 | 0.79
[5 empty] | 300 | 1.02 | 1.0167 | 0.9967 | 0.98 | 0.9633 | 0.9233 | 0.8533 | 0.8533 | 0.81
| searchcol | 6 |  |  | Weight of Water Calculation
| VolumeCol | 7
| WeightCol | 8
| densityCol | 10 |  |  | 1 gallon = .1337 cubic foot, 1 cu ft = 7.48 gallon | Percent Glycol 40: <-- from Machinery's Handbook pg 2447
| FirstRow | 283 |  |  | 7.4805 gallon = 1 cu ft | Percent Glycol 20: <-- fom Marks' Standard Handbook for Engineers , pg 1-31
| LastRow | 310 |  |  | therefore 1 gallon = .1336809 cu ft
| result |  | Volume
| result | 8.2087 | Weight |  | *** Use conversion from Marks' engineers handbook
| result |  | density
lb/gal = conversion (cu ft/gal) / specific volume (cu ft/lb)
Using Specific Volumes from 1993 ASHREA handbook, Fundamentals pgs 6.8 thru 6.10
and solving for the weight of water per gallon yields:
Density(lb/cu ft) = 1 / specific volume(cu ft/lb)
[5 empty] | Temp | Percent Glycol 10: volume cu ft/lb; Percent Glycol 20: lb/ gallon; Percent Glycol 40: Density lb/cu ft
[5 empty] | -30 | Percent Glycol 10: 0.01738; Percent Glycol 20: 7.6917; Percent Glycol 40: 57.5374
[5 empty] | -20 | Percent Glycol 10: 0.0174; Percent Glycol 20: 7.6828; Percent Glycol 40: 57.4713
[5 empty] | -10 | Percent Glycol 10: 0.01741; Percent Glycol 20: 7.6784; Percent Glycol 40: 57.4383
[5 empty] | 0 | Percent Glycol 10: 0.01743; Percent Glycol 20: 7.6696; Percent Glycol 40: 57.3723
[5 empty] | 10 | Percent Glycol 10: 0.01744; Percent Glycol 20: 7.6652; Percent Glycol 40: 57.3394
[5 empty] | 20 | Percent Glycol 10: 0.01746; Percent Glycol 20: 7.6564; Percent Glycol 40: 57.2738
[5 empty] | 30 | Percent Glycol 10: 0.01747; Percent Glycol 20: 7.652; Percent Glycol 40: 57.241
[5 empty] | 40 | Percent Glycol 10: 0.01602; Percent Glycol 20: 8.3446; Percent Glycol 40: 62.422
[5 empty] | 50 | Percent Glycol 10: 0.01602; Percent Glycol 20: 8.3446; Percent Glycol 40: 62.422
[5 empty] | 60 | Percent Glycol 10: 0.01604; Percent Glycol 20: 8.3342; Percent Glycol 40: 62.3441
[5 empty] | 70 | Percent Glycol 10: 0.01605; Percent Glycol 20: 8.329; Percent Glycol 40: 62.3053
[5 empty] | 80 | Percent Glycol 10: 0.01607; Percent Glycol 20: 8.3187; Percent Glycol 40: 62.2278
[5 empty] | 90 | Percent Glycol 10: 0.0161; Percent Glycol 20: 8.3032; Percent Glycol 40: 62.1118
[5 empty] | 100 | Percent Glycol 10: 0.01613; Percent Glycol 20: 8.2877; Percent Glycol 40: 61.9963
[5 empty] | 110 | Percent Glycol 10: 0.01617; Percent Glycol 20: 8.2672; Percent Glycol 40: 61.8429
[5 empty] | 120 | Percent Glycol 10: 0.0162; Percent Glycol 20: 8.2519; Percent Glycol 40: 61.7284
[5 empty] | 130 | Percent Glycol 10: 0.01625; Percent Glycol 20: 8.2265; Percent Glycol 40: 61.5385
[5 empty] | 140 | Percent Glycol 10: 0.01629; Percent Glycol 20: 8.2063; Percent Glycol 40: 61.3874
[5 empty] | 150 | Percent Glycol 10: 0.01634; Percent Glycol 20: 8.1812; Percent Glycol 40: 61.1995
[5 empty] | 160 | Percent Glycol 10: 0.01639; Percent Glycol 20: 8.1562; Percent Glycol 40: 61.0128
[5 empty] | 170 | Percent Glycol 10: 0.01645; Percent Glycol 20: 8.1265; Percent Glycol 40: 60.7903
[5 empty] | 180 | Percent Glycol 10: 0.01651; Percent Glycol 20: 8.097; Percent Glycol 40: 60.5694
[5 empty] | 190 | Percent Glycol 10: 0.01657; Percent Glycol 20: 8.0676; Percent Glycol 40: 60.35
[5 empty] | 200 | Percent Glycol 10: 0.01663; Percent Glycol 20: 8.0385; Percent Glycol 40: 60.1323
[5 empty] | 210 | Percent Glycol 10: 0.0167; Percent Glycol 20: 8.0048; Percent Glycol 40: 59.8802
[5 empty] | 220 | Percent Glycol 10: 0.01677; Percent Glycol 20: 7.9714; Percent Glycol 40: 59.6303
[5 empty] | 230 | Percent Glycol 10: 0.01684; Percent Glycol 20: 7.9383; Percent Glycol 40: 59.3824
[5 empty] | 240 | Percent Glycol 10: 0.01692; Percent Glycol 20: 7.9008; Percent Glycol 40: 59.1017
[5 empty] | 250 | Percent Glycol 10: 0.017; Percent Glycol 20: 7.8636; Percent Glycol 40: 58.8235
[5 empty] | 260 | Percent Glycol 10: 0.01708; Percent Glycol 20: 7.8268; Percent Glycol 40: 58.548
[5 empty] | 270 | Percent Glycol 10: 0.01717; Percent Glycol 20: 7.7857; Percent Glycol 40: 58.2411
[5 empty] | 280 | Percent Glycol 10: 0.01726; Percent Glycol 20: 7.7451; Percent Glycol 40: 57.9374
[5 empty] | 290 | Percent Glycol 10: 0.01735; Percent Glycol 20: 7.705; Percent Glycol 40: 57.6369
[5 empty] | 300 | Percent Glycol 10: 0.01745; Percent Glycol 20: 7.6608; Percent Glycol 40: 57.3066
| sheetname | HiddenTables |  |  | Weight of Ethylene Glycol Mixtures
| FindVertValue |  | temp
| findHorizValue |  | percent
| SeachCol | 6 | temp
| SearchRow | 321 | percent
| FirstRow | 330 |  |  |  | Percent Glycol 10: Percent Glycol
| LastRow | 357 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90
| FirstCol | 7 |  |  | Fluid | weight | weight | weight | weight | weight | weight | weight | weight | weight
| LastCol | 15 |  |  | Temp | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal)
| Result | 8.5616 | Weight |  | -30 | Percent Glycol 50: 9.1063; Percent Glycol 60: 9.228; Percent Glycol 70: 9.3443; Percent Glycol 80: 9.4579
[5 empty] | -20 | Percent Glycol 50: 9.097; Percent Glycol 60: 9.2186; Percent Glycol 70: 9.3336; Percent Glycol 80: 9.4446; Percent Glycol 90: 9.5515
[5 empty] | -10 |  |  |  | 8.962 | 9.0876 | 9.2066 | 9.3202 | 9.4299 | 9.5355
[5 empty] | 0 |  |  |  | 8.9526 | 9.0769 | 9.1946 | 9.3069 | 9.4151 | 9.5181
[5 empty] | 10 |  |  | 8.8136 | 8.9419 | 9.0636 | 9.1799 | 9.2908 | 9.3978 | 9.4994
|  |  | NOT USED !!!!!!! |  | 20 |  | 8.6665 | 8.8029 | 8.9299 | 9.0502 | 9.1652 | 9.2748 | 9.3791 | 9.4806
[5 empty] | 30 | 8.5141 | 8.6558 | 8.7909 | 8.9165 | 9.0355 | 9.1491 | 9.2574 | 9.3603 | 9.4593
[5 empty] | 40 | 8.5034 | 8.6438 | 8.7775 | 8.9018 | 9.0195 | 9.1317 | 9.2374 | 9.3389 | 9.4365
[5 empty] | 50 | 8.4914 | 8.6304 | 8.7628 | 8.8858 | 9.0021 | 9.113 | 9.2173 | 9.3176 | 9.4138
[5 empty] | 60 | 8.478 | 8.6157 | 8.7467 | 8.8684 | 8.9834 | 9.093 | 9.1959 | 9.2948 | 9.3884
[5 empty] | 70 | 8.4633 | 8.5997 | 8.7294 | 8.8497 | 8.9633 | 9.0716 | 9.1732 | 9.2708 | 9.363
[5 empty] | 80 | 8.4473 | 8.5837 | 8.712 | 8.8296 | 8.9433 | 9.0489 | 9.1491 | 9.244 | 9.3349
[5 empty] | 90 | 8.4313 | 8.5649 | 8.6919 | 8.8096 | 8.9205 | 9.0248 | 9.1237 | 9.2173 | 9.3069
[5 empty] | 100 | 8.4125 | 8.5462 | 8.6705 | 8.7868 | 8.8965 | 8.9994 | 9.097 | 9.1892 | 9.2775
[5 empty] | 110 | 8.3938 | 8.5248 | 8.6492 | 8.7641 | 8.8724 | 8.974 | 9.0689 | 9.1598 | 9.2467
[5 empty] | 120 | 8.3724 | 8.5034 | 8.6251 | 8.7387 | 8.8457 | 8.9459 | 9.0408 | 9.1291 | 9.2133
[5 empty] | 130 | 8.351 | 8.4794 | 8.601 | 8.7133 | 8.8189 | 8.9179 | 9.0101 | 9.097 | 9.1799
[5 empty] | 140 | 8.3283 | 8.4553 | 8.5756 | 8.6866 | 8.7895 | 8.8871 | 8.978 | 9.0649 | 9.1451
[5 empty] | 150 | 8.3029 | 8.4299 | 8.5489 | 8.6572 | 8.7601 | 8.8564 | 8.9459 | 9.0301 | 9.109
[5 empty] | 160 | 8.2775 | 8.4032 | 8.5195 | 8.6278 | 8.7294 | 8.8229 | 8.9112 | 8.9941 | 9.0716
[5 empty] | 170 | 8.2508 | 8.3738 | 8.4901 | 8.597 | 8.6959 | 8.7895 | 8.8764 | 8.958 | 9.0342
[5 empty] | 180 | 8.2227 | 8.3444 | 8.4593 | 8.5649 | 8.6625 | 8.7548 | 8.839 | 8.9192 | 8.9941
[5 empty] | 190 | 8.1933 | 8.3136 | 8.4272 | 8.5315 | 8.6278 | 8.7173 | 8.8016 | 8.8791 | 8.9526
[5 empty] | 200 | 8.1626 | 8.2815 | 8.3938 | 8.4968 | 8.5917 | 8.6799 | 8.7628 | 8.839 | 8.9098
[5 empty] | 210 | 8.1305 | 8.2494 | 8.3591 | 8.4607 | 8.5542 | 8.6411 | 8.7213 | 8.7975 | 8.8671
[5 empty] | 220 | 8.0971 | 8.2147 | 8.3243 | 8.4232 | 8.5155 | 8.601 | 8.6799 | 8.7534 | 8.8216
[5 empty] | 230 | 8.0623 | 8.1786 | 8.2869 | 8.3845 | 8.4754 | 8.5596 | 8.6371 | 8.7093 | 8.7762
[5 empty] | 240 | 8.0275 | 8.1412 | 8.2481 | 8.3457 | 8.4353 | 8.5168 | 8.593 | 8.6639 | 8.728
[5 empty] | 250 | 7.9901 | 8.1037 | 8.208 | 8.3043 | 8.3925 | 8.474 | 8.5476 | 8.6171 | 8.6799
[5 empty] | 260 | 7.9516 | 8.0687 | 8.1672 | 8.2618 | 8.3503 | 8.4258 | 8.501 | 8.5685 | 8.627
[5 empty] | 270 | 7.9121 | 8.0286 | 8.125 | 8.2182 | 8.3059 | 8.3793 | 8.453 | 8.519 | 8.5756
[5 empty] | 280 | 7.8713 | 7.9873 | 8.0815 | 8.1735 | 8.2602 | 8.3316 | 8.4038 | 8.4681 | 8.523
[5 empty] | 290 | 7.8293 | 7.9449 | 8.0367 | 8.1274 | 8.2134 | 8.2827 | 8.3532 | 8.416 | 8.4691
[5 empty] | 300 | 7.786 | 7.9013 | 7.9907 | 8.0801 | 8.1655 | 8.2326 | 8.3014 | 8.3626 | 8.4139
| sheetname | HiddenTables |  |  | Weight of Propylene Glycol Mixtures
| FindVertValue |  | temp
| findHorizValue |  | percent
| SeachCol | 6 | temp
| SearchRow | 371 | percent
| FirstRow | 380 |  |  |  | Percent Glycol 10: Percent Glycol
| LastRow | 407 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90
| FirstCol | 7 |  |  | Fluid | weight | weight | weight | weight | weight | weight | weight | weight | weight
| LastCol | 15 |  |  | Temp | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal) | (lb/gal)
| Result | 8.4065 | Weight |  | -30 | Percent Glycol 50: 0; Percent Glycol 60: 8.9633; Percent Glycol 70: 9.0195; Percent Glycol 80: 9.1411
[5 empty] | -20 | Percent Glycol 50: 8.8844; Percent Glycol 60: 8.9473; Percent Glycol 70: 9.0021; Percent Glycol 80: 9.1077; Percent Glycol 90: 9.0903
[5 empty] | -10 |  |  |  | 0 | 8.8697 | 8.9312 | 8.9834 | 9.0729 | 9.0569
[5 empty] | 0 |  |  |  | 8.7842 | 8.8537 | 8.9138 | 8.9633 | 9.0395 | 9.0221
[5 empty] | 10 |  |  | 8.6893 | 8.7695 | 8.8376 | 8.8951 | 8.9419 | 9.0047 | 8.9874
[5 empty] | 20 |  | 8.5863 | 8.6759 | 8.7534 | 8.8189 | 8.8737 | 8.9192 | 8.97 | 8.9526
[5 empty] | 30 | 8.5288 | 8.1733 | 8.6612 | 8.736 | 8.7989 | 8.8523 | 8.8951 | 8.9339 | 8.9179
[5 empty] | 40 | 8.462 | 8.5596 | 8.6451 | 8.7173 | 8.7788 | 8.8296 | 8.8697 | 8.8991 | 8.8818
[5 empty] | 50 | 8.4486 | 8.5449 | 8.6264 | 8.6973 | 8.7561 | 8.8056 | 8.8443 | 8.863 | 8.847
[5 empty] | 60 | 8.4353 | 8.5275 | 8.6077 | 8.6759 | 8.7334 | 8.7802 | 8.8163 | 8.8283 | 8.8109
[5 empty] | 70 | 8.4192 | 8.5101 | 8.5877 | 8.6532 | 8.708 | 8.7521 | 8.7868 | 8.7922 | 8.7748
[5 empty] | 80 | 8.4032 | 8.4914 | 8.5663 | 8.6291 | 8.6826 | 8.724 | 8.7574 | 8.7548 | 8.7387
[5 empty] | 90 | 8.3858 | 8.4714 | 8.5435 | 8.6037 | 8.6545 | 8.6946 | 8.7254 | 8.7187 | 8.7013
[5 empty] | 100 | 8.3671 | 8.4486 | 8.5195 | 8.577 | 8.6264 | 8.6639 | 8.6933 | 8.6826 | 8.6652
[5 empty] | 110 | 8.347 | 8.4259 | 8.4941 | 8.5489 | 8.5957 | 8.6318 | 8.6585 | 8.6451 | 8.6278
[5 empty] | 120 | 8.3256 | 8.4018 | 8.466 | 8.5208 | 8.5636 | 8.5984 | 8.6238 | 8.6077 | 8.5903
[5 empty] | 130 | 8.3029 | 8.3764 | 8.4379 | 8.4901 | 8.5315 | 8.5636 | 8.5863 | 8.5703 | 8.5529
[5 empty] | 140 | 8.2789 | 8.3497 | 8.4085 | 8.458 | 8.4981 | 8.5275 | 8.5489 | 8.5329 | 8.5155
[5 empty] | 150 | 8.2535 | 8.3216 | 8.3778 | 8.4246 | 8.462 | 8.4901 | 8.5101 | 8.4954 | 8.478
[5 empty] | 160 | 8.2267 | 8.2922 | 8.3457 | 8.3898 | 8.4259 | 8.4513 | 8.4687 | 8.4567 | 8.4393
[5 empty] | 170 | 8.1986 | 8.2615 | 8.3123 | 8.3537 | 8.3871 | 8.4112 | 8.4272 | 8.4179 | 8.4018
[5 empty] | 180 | 8.1692 | 8.2294 | 8.2775 | 8.3176 | 8.3484 | 8.3698 | 8.3845 | 8.3791 | 8.3631
[5 empty] | 190 | 8.1398 | 8.196 | 8.2414 | 8.2789 | 8.3069 | 8.327 | 8.3404 | 8.3404 | 8.3243
[5 empty] | 200 | 8.1077 | 8.1612 | 8.204 | 8.2388 | 8.2655 | 8.2842 | 8.2949 | 8.3016 | 8.2842
[5 empty] | 210 | 8.0757 | 8.1251 | 8.1652 | 8.1973 | 8.2214 | 8.2388 | 8.2468 | 8.2628 | 8.2454
[5 empty] | 220 | 8.0409 | 8.0877 | 8.1251 | 8.1545 | 8.1773 | 8.192 | 8.1986 | 8.2227 | 8.2053
[5 empty] | 230 | 8.0061 | 8.0489 | 8.0837 | 8.1118 | 8.1318 | 8.1438 | 8.1492 | 8.1826 | 8.1652
[5 empty] | 240 | 7.9687 | 8.0088 | 8.0409 | 8.0663 | 8.0837 | 8.0944 | 8.0984 | 8.1425 | 8.1251
[5 empty] | 250 | 7.9313 | 7.9674 | 7.9968 | 8.0075 | 8.0356 | 8.0449 | 8.0463 | 8.1024 | 8.085
[5 empty] | 260 | 7.8905 | 7.9204 | 7.9535 | 7.9625 | 7.9893 | 7.9916 | 7.9948 | 8.0628 | 8.0405
[5 empty] | 270 | 7.8501 | 7.8759 | 7.907 | 7.9098 | 7.9384 | 7.9384 | 7.9401 | 8.022 | 7.999
[5 empty] | 280 | 7.8084 | 7.8299 | 7.8593 | 7.8553 | 7.8861 | 7.8839 | 7.884 | 7.981 | 7.957
[5 empty] | 290 | 7.7656 | 7.7826 | 7.8102 | 7.7987 | 7.8325 | 7.8281 | 7.8267 | 7.9396 | 7.9148
[5 empty] | 300 | 7.7215 | 7.7339 | 7.7598 | 7.74 | 7.7776 | 7.771 | 7.768 | 7.898 | 7.8721
Viscosity of Water
| Sheetname | HiddenTables
| searchcol | 6 |  |  | Fluid | Percent Glycol 10: Viscosity; Percent Glycol 20: Viscosity
| DataCol | 8 |  |  | Temp | Percent Glycol 10: lb/ft hr; Percent Glycol 20: lb/ft sec
| FirstRow | 421 |  |  | 32 | Percent Glycol 10: 4.336; Percent Glycol 20: 0.0012044
| LastRow | 449 |  |  | 40 | Percent Glycol 10: 3.74; Percent Glycol 20: 0.0010389
| result | 0.00031698 | viscosity |  | 50 | Percent Glycol 10: 3.161; Percent Glycol 20: 0.00087806
| findvalue | 138.8 | awt |  | 60 | Percent Glycol 10: 2.713; Percent Glycol 20: 0.00075361
[5 empty] | 70 | Percent Glycol 10: 2.36; Percent Glycol 20: 0.00065556
[5 empty] | 80 | Percent Glycol 10: 2.075; Percent Glycol 20: 0.00057639
[5 empty] | 90 | Percent Glycol 10: 1.842; Percent Glycol 20: 0.00051167
[5 empty] | 100 | Percent Glycol 10: 1.648; Percent Glycol 20: 0.00045778
[5 empty] | 110 | Percent Glycol 10: 1.4886; Percent Glycol 20: 0.0004135
[5 empty] | 120 | Percent Glycol 10: 1.348; Percent Glycol 20: 0.00037444
[5 empty] | 130 | Percent Glycol 10: 1.23; Percent Glycol 20: 0.00034167
[5 empty] | 140 | Percent Glycol 10: 1.129; Percent Glycol 20: 0.00031361
[5 empty] | 150 | Percent Glycol 10: 1.04; Percent Glycol 20: 0.00028889
[5 empty] | 160 | Percent Glycol 10: 0.963; Percent Glycol 20: 0.0002675
[5 empty] | 170 | Percent Glycol 10: 0.894; Percent Glycol 20: 0.00024833
[5 empty] | 180 | Percent Glycol 10: 0.834; Percent Glycol 20: 0.00023167
[5 empty] | 190 | Percent Glycol 10: 0.781; Percent Glycol 20: 0.00021694
[5 empty] | 200 | Percent Glycol 10: 0.733; Percent Glycol 20: 0.00020361
[5 empty] | 210 | Percent Glycol 10: 0.69; Percent Glycol 20: 0.00019167
[5 empty] | 212 | Percent Glycol 10: 0.682; Percent Glycol 20: 0.00018944
[5 empty] | 220 | Percent Glycol 10: 0.651; Percent Glycol 20: 0.00018083
[5 empty] | 230 | Percent Glycol 10: 0.616; Percent Glycol 20: 0.00017111
[5 empty] | 240 | Percent Glycol 10: 0.585; Percent Glycol 20: 0.0001625
[5 empty] | 250 | Percent Glycol 10: 0.556; Percent Glycol 20: 0.00015444
[5 empty] | 260 | Percent Glycol 10: 0.53; Percent Glycol 20: 0.00014722
[5 empty] | 270 | Percent Glycol 10: 0.506; Percent Glycol 20: 0.00014056
[5 empty] | 280 | Percent Glycol 10: 0.484; Percent Glycol 20: 0.00013444
[5 empty] | 290 | Percent Glycol 10: 0.464; Percent Glycol 20: 0.00012889
[5 empty] | 300 | Percent Glycol 10: 0.445; Percent Glycol 20: 0.00012361
Viscosity of Ethylene Glycol
| sheetname | HiddenTables |  |  |  | Percent Glycol 10: Percent Glycol
| FindVertValue |  | temp |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90
| findHorizValue |  | percent |  | Fluid | Viscosity | Viscosity | Viscosity | Viscosity | Viscosity | Viscosity | Viscosity | Viscosity | Viscosity
| SeachCol | 6 | temp |  | Temp | (centipoise) | (centipoise) | (centipoise) | (centipoise) | (centipoise) | (centipoise) | (centipoise) | (centipoise) | (centipoise)
| SearchRow | 460 | percent |  | -30 | Percent Glycol 50: 63.69; Percent Glycol 60: 89.67; Percent Glycol 70: 128.79; Percent Glycol 80: 185.22
| FirstRow | 469 |  |  | -20 | Percent Glycol 50: 40.38; Percent Glycol 60: 60.46; Percent Glycol 70: 89.93; Percent Glycol 80: 131.32; Percent Glycol 90: 284.48
| LastRow | 496 |  |  | -10 |  |  |  | 19.58 | 27.27 | 42.05 | 63.5 | 91.88 | 169.83
| FirstCol | 7 |  |  | 0 |  |  |  | 13.76 | 19.34 | 30.08 | 45.58 | 65.04 | 107.77
| LastCol | 15 |  |  | 10 |  |  | 6.83 | 10.13 | 14.26 | 22.06 | 33.31 | 46.89 | 71.87
| Result | 0.00052685 | Viscosity |  | 20 |  | 3.9 | 5.38 | 7.74 | 10.85 | 16.56 | 24.79 | 34.48 | 49.94
[5 empty] | 30 | 2.16 | 3.14 | 4.33 | 6.09 | 8.48 | 12.68 | 19.77 | 25.84 | 35.91
[5 empty] | 40 | 1.82 | 2.59 | 3.54 | 4.91 | 6.77 | 9.9 | 14.45 | 19.71 | 26.59
[5 empty] | 50 | 1.56 | 2.18 | 2.95 | 4.04 | 5.5 | 7.85 | 11.31 | 15.29 | 20.18
|  |  | NOT USED !!!!!!! |  | 60 | 1.35 | 1.86 | 2.49 | 3.38 | 4.55 | 6.33 | 8.97 | 12.05 | 15.65
[5 empty] | 70 | 1.18 | 1.61 | 2.13 | 2.87 | 3.81 | 5.17 | 7.22 | 9.62 | 12.37
[5 empty] | 80 | 1.04 | 1.41 | 1.84 | 2.46 | 3.23 | 4.28 | 5.88 | 7.79 | 9.93
[5 empty] | 90 | 0.93 | 1.24 | 1.6 | 2.13 | 2.76 | 3.58 | 4.85 | 6.38 | 8.1
[5 empty] | 100 | 0.83 | 1.11 | 1.41 | 1.87 | 2.39 | 3.03 | 4.04 | 5.28 | 6.68
[5 empty] | 110 | 0.75 | 0.99 | 1.25 | 1.64 | 2.08 | 2.58 | 3.4 | 4.41 | 5.58
[5 empty] | 120 | 0.69 | 0.9 | 1.11 | 1.46 | 1.82 | 2.33 | 2.88 | 3.73 | 4.71
[5 empty] | 130 | 0.62 | 0.81 | 1 | 1.3 | 1.61 | 1.93 | 2.47 | 3.17 | 4.01
[5 empty] | 140 | 0.57 | 0.74 | 0.9 | 1.17 | 1.43 | 1.69 | 2.13 | 2.72 | 3.45
[5 empty] | 150 | 0.53 | 0.68 | 0.82 | 1.05 | 1.28 | 1.49 | 1.86 | 2.35 | 2.98
[5 empty] | 160 | 0.49 | 0.63 | 0.75 | 0.95 | 1.15 | 1.32 | 1.63 | 2.05 | 2.6
[5 empty] | 170 | 0.46 | 0.58 | 0.68 | 0.87 | 1.04 | 1.18 | 1.43 | 1.8 | 2.28
[5 empty] | 180 | 0.43 | 0.54 | 0.63 | 0.79 | 0.94 | 1.06 | 1.27 | 1.58 | 2.01
[5 empty] | 190 | 0.4 | 0.5 | 0.58 | 0.73 | 0.85 | 0.95 | 1.14 | 1.4 | 1.79
[5 empty] | 200 | 0.37 | 0.47 | 0.54 | 0.67 | 0.78 | 0.86 | 1.02 | 1.25 | 1.6
[5 empty] | 210 | 0.35 | 0.43 | 0.5 | 0.61 | 0.71 | 0.78 | 0.92 | 1.12 | 1.43
[5 empty] | 220 | 0.33 | 0.41 | 0.46 | 0.57 | 0.66 | 0.72 | 0.83 | 1.01 | 1.29
[5 empty] | 230 | 0.32 | 0.38 | 0.43 | 0.53 | 0.6 | 0.66 | 0.76 | 0.91 | 1.16
[5 empty] | 240 | 0.3 | 0.36 | 0.4 | 0.49 | 0.56 | 0.61 | 0.69 | 0.83 | 1.06
[5 empty] | 250 | 0.29 | 0.34 | 0.38 | 0.45 | 0.52 | 0.56 | 0.63 | 0.75 | 0.96
[5 empty] | 260 | 0.274 | 0.3172 | 0.3517 | 0.4081 | 0.4483 | 0.4793 | 0.5328 | 0.6345 | 0.8207
[5 empty] | 270 | 0.258 | 0.2912 | 0.3197 | 0.3641 | 0.3953 | 0.4183 | 0.4538 | 0.5335 | 0.6917
[5 empty] | 280 | 0.242 | 0.2652 | 0.2877 | 0.3201 | 0.3423 | 0.3573 | 0.3748 | 0.4325 | 0.5627
[5 empty] | 290 | 0.226 | 0.2392 | 0.2557 | 0.2761 | 0.2893 | 0.2963 | 0.2958 | 0.3315 | 0.4337
[5 empty] | 300 | 0.21 | 0.2132 | 0.2237 | 0.2321 | 0.2363 | 0.2353 | 0.2168 | 0.2305 | 0.3047
convert from centipoisies to lb/ft sec: mult by .000672
Viscosity of Propylene Glycol
| sheetname | HiddenTables |  |  |  | Percent Glycol 10: Percent Glycol
| FindVertValue |  | temp |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90
| findHorizValue |  | percent |  | Fluid | Viscosity | Viscosity | Viscosity | Viscosity | Viscosity | Viscosity | Viscosity | Viscosity | Viscosity
| SeachCol | 6 | temp |  | Temp | (centipoise) | (centipoise) | (centipoise) | (centipoise) | (centipoise) | (centipoise) | (centipoise) | (centipoise) | (centipoise)
| SearchRow | 510 | percent |  | -30 | Percent Glycol 60: 497.57; Percent Glycol 70: 864.87; Percent Glycol 80: 1363.75; Percent Glycol 90: 3555.22
| FirstRow | 519 |  |  | -20 | Percent Glycol 50: 156.08; Percent Glycol 60: 298.75; Percent Glycol 70: 493.93; Percent Glycol 80: 820.58; Percent Glycol 90: 1819.72
| LastRow | 546 |  |  | -10 | Percent Glycol 50: 95.97; Percent Glycol 60: 182.96; Percent Glycol 70: 291.28; Percent Glycol 80: 495.68; Percent Glycol 90: 983.05
| FirstCol | 7 |  |  | 0 |  |  |  | 40.99 | 61.32 | 114.9 | 177.73 | 303.94 | 558.32
| LastCol | 15 |  |  | 10 |  |  | 13.44 | 27.17 | 40.62 | 74.19 | 112.2 | 190.41 | 332.02
| Result | 0.0008568 | Viscosity |  | 20 |  | 5.36 | 9.91 | 18.64 | 27.83 | 49.29 | 73.22 | 122.3 | 205.91
[5 empty] | 30 | 2.8 | 4.23 | 7.47 | 13.2 | 19.66 | 33.68 | 49.32 | 80.66 | 132.67
[5 empty] | 40 | 2.28 | 3.41 | 5.75 | 9.63 | 14.28 | 23.65 | 34.22 | 54.64 | 88.51
[5 empty] | 50 | 1.89 | 2.79 | 4.52 | 7.22 | 10.65 | 17.05 | 24.41 | 37.99 | 60.93
[5 empty] | 60 | 1.6 | 2.32 | 3.61 | 5.55 | 8.13 | 12.59 | 17.86 | 27.1 | 43.16
[5 empty] | 70 | 1.38 | 1.95 | 2.94 | 4.36 | 6.34 | 9.51 | 13.38 | 19.79 | 31.37
[5 empty] | 80 | 1.2 | 1.66 | 2.43 | 3.5 | 5.04 | 7.34 | 10.25 | 14.79 | 23.35
[5 empty] | 90 | 1.05 | 1.43 | 2.04 | 2.86 | 4.08 | 5.77 | 8 | 11.29 | 17.75
[5 empty] | 100 | 0.93 | 1.25 | 1.73 | 2.37 | 3.35 | 4.62 | 6.37 | 8.79 | 13.76
[5 empty] | 110 | 0.83 | 1.1 | 1.49 | 2 | 2.79 | 3.76 | 5.15 | 6.97 | 10.86
[5 empty] | 120 | 0.75 | 0.97 | 1.3 | 1.71 | 2.36 | 3.11 | 4.23 | 5.62 | 8.71
[5 empty] | 130 | 0.68 | 0.87 | 1.14 | 1.49 | 2.02 | 2.61 | 3.53 | 4.6 | 7.09
[5 empty] | 140 | 0.62 | 0.78 | 1.01 | 1.3 | 1.75 | 2.22 | 2.98 | 3.82 | 5.85
[5 empty] | 150 | 0.57 | 0.71 | 0.9 | 1.16 | 1.53 | 1.91 | 2.54 | 3.22 | 4.89
[5 empty] | 160 | 0.52 | 0.64 | 0.82 | 1.03 | 1.35 | 1.66 | 2.19 | 2.75 | 4.13
[5 empty] | 170 | 0.48 | 0.59 | 0.74 | 0.93 | 1.2 | 1.45 | 1.91 | 2.37 | 3.52
[5 empty] | 180 | 0.44 | 0.54 | 0.68 | 0.85 | 1.08 | 1.29 | 1.69 | 2.07 | 3.04
[5 empty] | 190 | 0.41 | 0.5 | 0.62 | 0.78 | 0.97 | 1.15 | 1.5 | 1.82 | 2.64
[5 empty] | 200 | 0.38 | 0.46 | 0.58 | 0.72 | 0.88 | 1.04 | 1.34 | 1.61 | 2.31
[5 empty] | 210 | 0.36 | 0.43 | 0.54 | 0.67 | 0.81 | 0.94 | 1.21 | 1.45 | 2.04
[5 empty] | 220 | 0.34 | 0.4 | 0.5 | 0.62 | 0.74 | 0.86 | 1.1 | 1.31 | 1.82
[5 empty] | 230 | 0.32 | 0.38 | 0.47 | 0.59 | 0.69 | 0.79 | 1 | 1.19 | 1.63
[5 empty] | 240 | 0.3 | 0.36 | 0.45 | 0.55 | 0.64 | 0.73 | 0.92 | 1.09 | 1.47
[5 empty] | 250 | 0.28 | 0.34 | 0.42 | 0.52 | 0.59 | 0.68 | 0.85 | 1 | 1.33
[5 empty] | 260 | 0.26 | 0.3181 | 0.3917 | 0.4483 | 0.5362 | 0.5909 | 0.7381 | 0.8662 | 1.1062
[5 empty] | 270 | 0.24 | 0.2941 | 0.3597 | 0.3953 | 0.4782 | 0.5179 | 0.6391 | 0.7432 | 0.9082
[5 empty] | 280 | 0.22 | 0.2701 | 0.3277 | 0.3423 | 0.4202 | 0.4449 | 0.5401 | 0.6202 | 0.7102
[5 empty] | 290 | 0.2 | 0.2461 | 0.2957 | 0.2893 | 0.3622 | 0.3719 | 0.4411 | 0.4972 | 0.5122
[5 empty] | 300 | 0.18 | 0.2221 | 0.2637 | 0.2363 | 0.3042 | 0.2989 | 0.3421 | 0.3742 | 0.3142
convert from centipoisies to lb/ft sec: mult by .000672
Reynolds # vs Friction Factor
| searchcol | 6
| DataCol | 7 |  |  | from Moody chart,
| FirstRow | 564 |  |  | source: Engineering Formulas, 6th edition, K. Gieck & R. Gieck, page Z8
| LastRow | 572
| result | 0.048465 | friction factor |  | Re | Percent Glycol 10: smooth pipe (f)
| findvalue | 2174.5837 | reynolds |  | 2300 | Percent Glycol 10: 0.048
[5 empty] | 5000 | Percent Glycol 10: 0.038
[5 empty] | 10000 | Percent Glycol 10: 0.032
[5 empty] | 50000 | Percent Glycol 10: 0.022
[5 empty] | 100000 | Percent Glycol 10: 0.018
[5 empty] | 500000 | Percent Glycol 10: 0.014
[5 empty] | 1000000 | Percent Glycol 10: 0.011
[5 empty] | 5000000 | Percent Glycol 10: 0.0091
[5 empty] | 10000000 | Percent Glycol 10: 0.0082
Equivalent Lenghts for Head Loss Calc.
(determined by trial and error per catalog data, using work area below)
[5 empty] | size | Percent Glycol 10: 1 row equiv. ft; Percent Glycol 20: 2 row equiv ft; Percent Glycol 40: tube id
[5 empty] | 02 | Percent Glycol 10: 158; Percent Glycol 20: 220; Percent Glycol 40: 1.313
[5 empty] | 03 | Percent Glycol 10: 178; Percent Glycol 20: 245
[5 empty] | 04 | Percent Glycol 10: 190; Percent Glycol 20: 260
[5 empty] | 06 | Percent Glycol 10: 212; Percent Glycol 20: 310
[5 empty] | 08 | Percent Glycol 10: 225; Percent Glycol 20: 325
[5 empty] | 10 | Percent Glycol 10: 230; Percent Glycol 20: 337
[5 empty] | 12 | Percent Glycol 10: 240; Percent Glycol 20: 360
[5 empty] | 14 | Percent Glycol 10: 260; Percent Glycol 20: 395
PRELIMINARY

## HiddenUnitData (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41
Original data!!!!
| HOT WATER - UNIT TABLE | [15 empty] | HOT WATER - UNIT TABLE
| NOTE: THIS DATA TABLE WAS TAKEN FROM TABLE I, VULCAN CATALOG 415.12 (USED MBH AND CFM DATA) OR DERIVED FROM TABLE II & III | [15 empty] | NOTE: THIS DATA TABLE WAS DERIVED FROM TABLE II, VULCAN CATALOG 415.10 (USED MBH AND CFM DATA)
FAT IS CALCULATED
|  | UNIT |  | WATER | [12 empty] | UNIT |  | WATER | [7 empty] | COIL
|  | SIZE | GPM | P.D./FT. | CFM | MBH | WTDº | FATº | EATº | EWTº | COIL | [5 empty] | SIZE | GPM | P.D./FT. | SPEED | CFM | MBH | WTDº | FATº | EATº | EWTº | - - - -
|  | 02 | 1.64 | 0.184 | 230 | 16.4 | 20 | 125.7183 | 60 | 200 | 1 ROW | [5 empty] | 2 | 1.72 | 0.18 | HIGH | 230 | 16.7 | 20 | 126.7 | 60 | 200 | 1 ROW
|  | 03 | 2.28 | 0.36 | 335 | 22.8 | 20 | 122.7278 | 60 | 200 | 1 ROW | [5 empty] | 3 | 2.4 | 0.36 | HIGH | 335 | 23.3 | 20 | 124 | 60 | 200 | 1 ROW
|  | 02 | 2.58 | 0.53 | 225 | 25.8 | 20 | 165.6836 | 60 | 200 | 2 ROW | [5 empty] | 2 | 2.67 | 0.53 | HIGH | 225 | 25.8 | 20 | 165.8 | 60 | 200 | 2 ROW
|  | 04 | 2.98 | 0.58 | 430 | 29.8 | 20 | 123.8731 | 60 | 200 | 1 ROW | [5 empty] | 4 | 3.08 | 0.58 | HIGH | 430 | 29.8 | 20 | 123.8 | 60 | 200 | 1 ROW
|  | 03 | 3.54 | 0.98 | 330 | 35.383 | 20 | 158.8214 | 60 | 200 | 2 ROW | [5 empty] | 3 | 3.65 | 0.98 | HIGH | 330 | 35.4 | 20 | 158.8 | 60 | 200 | 2 ROW
|  | 04 | 4.63 | 1.7 | 420 | 46.3 | 20 | 161.6019 | 60 | 200 | 2 ROW | [5 empty] | 4 | 4.79 | 1.7 | HIGH | 420 | 46.3 | 20 | 161.7 | 60 | 200 | 2 ROW
|  | 06 | 4.8 | 1.54 | 630 | 48 | 20 | 130.2216 | 60 | 200 | 1 ROW | [5 empty] | 6 | 5.09 | 1.54 | HIGH | 630 | 49.3 | 20 | 132.1 | 60 | 200 | 1 ROW
|  | 08 | 5.45 | 2.02 | 860 | 54.5 | 20 | 118.4075 | 60 | 200 | 1 ROW | [5 empty] | 8 | 5.75 | 2.02 | HIGH | 860 | 55.6 | 20 | 119.6 | 60 | 200 | 1 ROW
|  | 10 | 6.2 | 2.51 | 1060 | 62 | 20 | 113.9084 | 60 | 200 | 1 ROW | [5 empty] | 10 | 6.45 | 2.51 | HIGH | 1060 | 62.5 | 20 | 114.3 | 60 | 200 | 1 ROW
|  | 06 | 6.98 | 4.1 | 620 | 69.8 | 20 | 163.761 | 60 | 200 | 2 ROW | [5 empty] | 6 | 7.21 | 4.1 | HIGH | 620 | 69.8 | 20 | 163.7 | 60 | 200 | 2 ROW
|  | 12 | 7.56 | 3.77 | 1230 | 75.6 | 20 | 116.6483 | 60 | 200 | 1 ROW | [5 empty] | 12 | 7.89 | 3.77 | HIGH | 1230 | 76.4 | 20 | 117.2 | 60 | 200 | 1 ROW
|  | 14 | 7.85 | 4.42 | 1410 | 78.5 | 20 | 111.3122 | 60 | 200 | 1 ROW | [5 empty] | 14 | 8.22 | 4.42 | HIGH | 1410 | 79.6 | 20 | 112 | 60 | 200 | 1 ROW
|  | 08 | 8.76 | 6.62 | 845 | 87.6 | 20 | 155.5471 | 60 | 200 | 2 ROW | [5 empty] | 8 | 9.04 | 6.62 | HIGH | 845 | 87.6 | 20 | 155.2 | 60 | 200 | 2 ROW
|  | 10 | 10.18 | 9.12 | 1040 | 101.8 | 20 | 150.2162 | 60 | 200 | 2 ROW | [5 empty] | 10 | 10.52 | 9.12 | HIGH | 1040 | 101.8 | 20 | 150.2 | 60 | 200 | 2 ROW
|  | 12 | 11.98 | 13.21 | 1210 | 119.8 | 20 | 151.2519 | 60 | 200 | 2 ROW | [5 empty] | 12 | 12.37 | 13.21 | HIGH | 1210 | 119.8 | 20 | 151.3 | 60 | 200 | 2 ROW
|  | 14 | 12.86 | 16.52 | 1385 | 128.6 | 20 | 145.5779 | 60 | 200 | 2 ROW | [5 empty] | 14 | 13.28 | 16.52 | HIGH | 1385 | 128.6 | 20 | 145.6 | 60 | 200 | 2 ROW
STEAM - UNIT TABLE
DATA FROM TABLE I VULCAN CATALOG 415.12
|  | UNIT |  | COND. |  |  | MBH |  |  |  |  | MBH= (Cond. LB/Hr * Latent Heat of steam at conditional pressure)/1000
|  | SIZE | EDR | LB/HR | PSI | CFM | @ 2 PSI | FATº | EATº |  |  | Note: for 2 psi steam the latent heat is 966.3
|  | 02 | 94.2142 | 23.4 | 2 | 230 | 22.6114 | 150.6088 | 60 |  |  | 1000 is the conversion from Btu to MBH
|  | 03 | 130.8531 | 32.5 | 2 | 335 | 31.4047 | 146.4014 | 60
|  | 04 | 170.713 | 42.4 | 2 | 430 | 40.9711 | 147.8172 | 60 |  |  | EDR = (MBH * 1000 Btu/MBH)/240
|  | 06 | 275.3955 | 68.4 | 2 | 630 | 66.0949 | 156.6936 | 60
|  | 08 | 312.8396 | 77.7 | 2 | 860 | 75.0815 | 140.4646 | 60 |  |  | FAT = (MBH * 1000 Btu/MBH)/(1.085 * CFM) + EAT
|  | 10 | 355.9205 | 88.4 | 2 | 1060 | 85.4209 | 134.2726 | 60
|  | 12 | 433.6271 | 107.7 | 2 | 1230 | 104.0705 | 137.9817 | 60
|  | 14 | 450.94 | 112 | 2 | 1410 | 108.2256 | 130.7426 | 60
CABINET UNIT HEATERS
data tables |  |  |  | HEATING CAPACITIES
for calculation |  |  |  | TABLE II - STANDARD COIL | [9 empty] | ENTERING WATER - 200º F
ENTERING AIR - 60º F
|  |  |  | UNIT |  | WATER | HIGH FAN SPEED |  |  |  | LOW FAN SPEED |  |  |  |  | UNIT |  | WATER | HIGH FAN SPEED |  |  |  | LOW FAN SPEED
|  |  |  | SIZE | GPM | P.D./FT. | CFM | MBH | WTD | FAT | CFM | MBH | WTD | FAT |  | SIZE | GPM | P.D./FT. | CFM | MBH | WTD | FAT | CFM | MBH | WTD | FAT
[5 empty] | 0.55 | 0.02 |  | 12.8 | 51.2 | 111 |  | 11.8 | 47.2 | 119 |  |  | 2.59 | 0.36 |  | 18.8 | 15 | 135 |  | 17.3 | 13.8 | 146
[5 empty] | 1.03 | 0.07 |  | 15.1 | 30.2 | 120 |  | 13.8 | 27.6 | 129 |  |  | 2.07 | 0.24 |  | 17.4 | 17.4 | 130 |  | 16.1 | 16.1 | 140
|  |  |  | 02 | 1.55 | 0.15 | 230 | 16.2 | 21.6 | 125 | 185 | 15 | 20 | 135 |  | 02 | 1.55 | 0.15 | 230 | 16.2 | 21.6 | 125 | 185 | 15 | 20 | 135
[5 empty] | 2.07 | 0.24 |  | 17.4 | 17.4 | 130 |  | 16.1 | 16.1 | 140 |  |  | 1.03 | 0.07 |  | 15.1 | 30.2 | 120 |  | 13.8 | 27.6 | 129
[5 empty] | 2.59 | 0.36 |  | 18.8 | 15 | 135 |  | 17.3 | 13.8 | 146 |  |  | 0.51 | 0.02 |  | 12.8 | 51.2 | 111 |  | 11.8 | 47.2 | 119
[5 empty] | 1.03 | 0.08 |  | 21.3 | 42.6 | 118 |  | 19.1 | 38.2 | 125 |  |  | 3.11 | 0.55 |  | 23.8 | 15.8 | 126 |  | 21.1 | 14.1 | 132
[5 empty] | 1.55 | 0.16 |  | 21.9 | 28.9 | 120 |  | 19.8 | 26.4 | 128 |  |  | 2.58 | 0.4 |  | 23.5 | 18.8 | 125 |  | 20.7 | 16.6 | 131
|  |  |  | 03 | 2.06 | 0.28 | 335 | 22.7 | 22.7 | 122 | 270 | 20.1 | 20.1 | 129 |  | 03 | 2.06 | 0.28 | 335 | 22.7 | 22.7 | 122 | 270 | 20.1 | 20.1 | 129
[5 empty] | 2.58 | 0.4 |  | 23.5 | 18.8 | 125 |  | 20.7 | 16.6 | 131 |  |  | 1.55 | 0.16 |  | 21.9 | 28.9 | 120 |  | 19.8 | 26.4 | 128
[5 empty] | 3 | 0.55 |  | 23.8 | 15.8 | 126 |  | 21.1 | 14.1 | 132 |  |  | 1.03 | 0.08 |  | 21.3 | 42.6 | 118 |  | 19.1 | 38.2 | 125
[5 empty] | 1.03 | 0.08 |  | 21.8 | 43.6 | 106 |  | 19 | 38 | 111 |  |  | 5.18 | 1.42 |  | 32.3 | 12.9 | 129 |  | 28.3 | 11.3 | 136
[5 empty] | 2.06 | 0.29 |  | 26.6 | 26.6 | 117 |  | 23.9 | 23.9 | 124 |  |  | 4.14 | 0.95 |  | 30.9 | 15.4 | 126 |  | 27.4 | 13.7 | 133
|  |  |  | 04 | 2.59 | 0.43 | 430 | 29 | 23.2 | 122 | 345 | 25.8 | 20.5 | 129 |  | 04 | 2.59 | 0.43 | 430 | 29 | 23.2 | 122 | 345 | 25.8 | 20.5 | 129
[5 empty] | 4.14 | 0.95 |  | 30.9 | 15.4 | 126 |  | 27.4 | 13.7 | 133 |  |  | 2.06 | 0.29 |  | 26.6 | 26.6 | 117 |  | 23.9 | 23.9 | 124
[5 empty] | 5.18 | 1.42 |  | 32.3 | 12.9 | 129 |  | 28.3 | 11.3 | 136 |  |  | 1.03 | 0.08 |  | 21.8 | 43.6 | 106 |  | 19 | 38 | 111
[5 empty] | 2.07 | 0.33 |  | 40.4 | 40.4 | 119 |  | 35.7 | 35.7 | 125 |  |  | 6.17 | 2.14 |  | 50.7 | 16.9 | 134 |  | 44.6 | 15 | 142
[5 empty] | 3.1 | 0.66 |  | 44.8 | 29.8 | 125 |  | 39.8 | 26.5 | 133 |  |  | 5.15 | 1.57 |  | 49.4 | 19.8 | 132 |  | 43.6 | 17.5 | 140
|  |  |  | 06 | 4.12 | 1.06 | 630 | 47.2 | 23.6 | 129 | 505 | 41.9 | 21 | 136 |  | 06 | 4.12 | 1.06 | 630 | 47.2 | 23.6 | 129 | 505 | 41.9 | 21 | 136
[5 empty] | 5.15 | 1.57 |  | 49.4 | 19.8 | 132 |  | 43.6 | 17.5 | 140 |  |  | 3.1 | 0.66 |  | 44.8 | 29.8 | 125 |  | 39.8 | 26.5 | 133
[5 empty] | 6.17 | 2.14 |  | 50.7 | 16.9 | 134 |  | 44.6 | 15 | 142 |  |  | 2.07 | 0.33 |  | 40.4 | 40.4 | 119 |  | 35.7 | 35.7 | 125
[5 empty] | 2.06 | 0.35 |  | 47.1 | 47.1 | 110 |  | 42 | 42 | 117 |  |  | 8.28 | 3.87 |  | 57.8 | 14.4 | 122 |  | 51.2 | 12.8 | 129
[5 empty] | 3.09 | 0.7 |  | 52.2 | 34.8 | 115 |  | 46.5 | 31 | 123 |  |  | 6.19 | 2.29 |  | 56 | 18.6 | 120 |  | 49.1 | 16.4 | 126
|  |  |  | 08 | 4.12 | 1.13 | 860 | 53.9 | 26.9 | 117 | 685 | 48.3 | 24.2 | 125 |  | 08 | 4.12 | 1.13 | 860 | 53.9 | 26.9 | 117 | 685 | 48.3 | 24.2 | 125
[5 empty] | 6.2 | 2.29 |  | 56 | 18.6 | 120 |  | 49.1 | 16.4 | 126 |  |  | 3.09 | 0.7 |  | 52.2 | 34.8 | 115 |  | 46.5 | 31 | 123
[5 empty] | 8.28 | 3.87 |  | 57.8 | 14.4 | 122 |  | 51.2 | 12.8 | 129 |  |  | 2.06 | 0.35 |  | 47.1 | 47.1 | 110 |  | 42 | 42 | 117
[5 empty] | 3.09 | 0.72 |  | 52.1 | 34.7 | 105.3 |  | 50.2 | 33.5 | 115 |  |  | 10.33 | 6.01 |  | 66 | 13.2 | 117 |  | 58.9 | 11.8 | 124
[5 empty] | 4.12 | 1.15 |  | 60.4 | 30.2 | 112 |  | 53.5 | 26.8 | 118 |  |  | 8.27 | 3.94 |  | 64.1 | 16 | 116 |  | 56.3 | 14.1 | 121
|  |  |  | 10 | 6.21 | 2.35 | 1060 | 62.2 | 20.7 | 114 | 845 | 54.7 | 18.2 | 120 |  | 10 | 6.21 | 2.35 | 1060 | 62.2 | 20.7 | 114 | 845 | 54.7 | 18.2 | 120
[5 empty] | 8.27 | 3.94 |  | 64.1 | 16 | 116 |  | 56.3 | 14.1 | 121 |  |  | 4.12 | 1.15 |  | 60.4 | 30.2 | 112 |  | 53.5 | 26.8 | 118
[5 empty] | 10.33 | 6.01 |  | 66 | 13.2 | 117 |  | 58.9 | 11.8 | 124 |  |  | 3.09 | 0.72 |  | 52.1 | 34.7 | 105.3 |  | 50.2 | 33.5 | 115
[5 empty] | 4.12 | 1.21 |  | 71.5 | 35.7 | 113 |  | 65.1 | 32.6 | 131 |  |  | 12.42 | 8.83 |  | 78.6 | 13.1 | 119 |  | 69.7 | 11.6 | 136
[5 empty] | 6.2 | 2.45 |  | 74.5 | 24.8 | 116 |  | 66.6 | 22.2 | 133 |  |  | 10.35 | 6.29 |  | 77.7 | 15.5 | 118 |  | 69 | 13.8 | 135
|  |  |  | 12 | 8.28 | 4.13 | 1230 | 76.7 | 19.1 | 117 | 985 | 68 | 17 | 134 |  | 12 | 8.28 | 4.13 | 1230 | 76.7 | 19.1 | 117 | 985 | 68 | 17 | 134
[5 empty] | 10.35 | 6.29 |  | 77.7 | 15.5 | 118 |  | 69 | 13.8 | 135 |  |  | 6.2 | 2.45 |  | 74.5 | 24.8 | 116 |  | 66.6 | 22.2 | 133
[5 empty] | 12.42 | 8.83 |  | 78.6 | 13.1 | 119 |  | 69.7 | 11.6 | 136 |  |  | 4.12 | 1.21 |  | 71.5 | 35.7 | 113 |  | 65.1 | 32.6 | 131
[5 empty] | 3.6 | 1.03 |  | 71 | 40.6 | 106 |  | 66.3 | 37.9 | 114 |  |  | 12.4 | 9.55 |  | 81.7 | 13.6 | 113 |  | 73 | 12.2 | 120
[5 empty] | 4.12 | 1.31 |  | 74.1 | 37 | 108 |  | 68.4 | 34.2 | 116 |  |  | 10.33 | 6.8 |  | 80.9 | 16.2 | 113 |  | 72.5 | 14.5 | 119
|  |  |  | 14 | 6.18 | 2.66 | 1410 | 77.6 | 25.9 | 111 | 1130 | 69.9 | 23.3 | 117 |  | 14 | 6.18 | 2.66 | 1410 | 77.6 | 25.9 | 111 | 1130 | 69.9 | 23.3 | 117
[5 empty] | 10.33 | 6.8 |  | 80.9 | 16.2 | 113 |  | 72.5 | 14.5 | 119 |  |  | 4.12 | 1.31 |  | 74.1 | 37 | 108 |  | 68.4 | 34.2 | 116
[5 empty] | 12.4 | 9.55 |  | 81.7 | 13.6 | 113 |  | 73 | 12.2 | 120 |  |  | 3.6 | 1.03 |  | 71 | 40.6 | 106 |  | 66.3 | 37.9 | 114
CABINET UNIT HEATERS
HEATING CAPACITIES
|  |  |  | TABLE III - HIGH CAPACITIY - 2 ROW COIL |  |  | LOW FAN SPEED FAT: ENTERING WATER - 200º F |  | TABLE III - HIGH CAPACITIY - 2 ROW COIL | [9 empty] | ENTERING WATER - 200º F
[7 empty] | LOW FAN SPEED FAT: ENTERING AIR - 60º F | [11 empty] | ENTERING AIR - 60º F
|  |  |  | UNIT |  | WATER | HIGH FAN SPEED CFM: HIGH FAN SPEED; LOW FAN SPEED CFM: LOW FAN SPEED |  | UNIT |  | WATER | HIGH FAN SPEED |  |  |  | LOW FAN SPEED
|  |  |  | SIZE | GPM | P.D./FT. | CFM | MBH | WTD | FAT | CFM | MBH | WTD | FAT |  | SIZE | GPM | P.D./FT. | CFM | MBH | WTD | FAT | CFM | MBH | WTD | FAT
[5 empty] | 0.51 | 0.02 |  | 17.9 | 71.6 | 133 |  | 16.5 | 66 | 144 |  |  | 2.58 | 0.5 |  | 25.7 | 20.6 | 165 |  | 23.5 | 18.8 | 180
[5 empty] | 1.03 | 0.1 |  | 21.7 | 43.4 | 149 |  | 19.9 | 39.8 | 162 |  |  | 2.06 | 0.34 |  | 24.8 | 24.8 | 162 |  | 22.5 | 22.5 | 175
|  |  |  | 02 | 1.54 | 0.2 | 225 | 23.3 | 31.1 | 155 | 180 | 21.4 | 28.5 | 170 |  | 02 | 1.54 | 0.2 | 225 | 23.3 | 31.1 | 155 | 180 | 21.4 | 28.5 | 170
[5 empty] | 2.06 | 0.34 |  | 24.8 | 24.8 | 162 |  | 22.5 | 22.5 | 175 |  |  | 1.03 | 0.1 |  | 21.7 | 43.4 | 149 |  | 19.9 | 39.8 | 162
[5 empty] | 2.58 | 0.5 |  | 25.7 | 20.6 | 165 |  | 23.5 | 18.8 | 180 |  |  | 0.51 | 0.02 |  | 17.9 | 71.6 | 133 |  | 16.5 | 66 | 144
[5 empty] | 1.03 | 0.11 |  | 30.1 | 60.2 | 144 |  | 28.3 | 56.6 | 158 |  |  | 3.09 | 0.75 |  | 34.9 | 23.3 | 157 |  | 30.8 | 20.5 | 167
[5 empty] | 1.54 | 0.23 |  | 31.9 | 42.5 | 149 |  | 28.9 | 38.5 | 161 |  |  | 2.58 | 0.56 |  | 34.3 | 27.4 | 156 |  | 30.3 | 24.2 | 165
|  |  |  | 03 | 2.06 | 0.38 | 330 | 33.1 | 33.1 | 152 | 265 | 29.7 | 29.7 | 163 |  | 03 | 2.06 | 0.38 | 330 | 33.1 | 33.1 | 152 | 265 | 29.7 | 29.7 | 163
[5 empty] | 2.58 | 0.56 |  | 34.3 | 27.4 | 156 |  | 30.3 | 24.2 | 165 |  |  | 1.54 | 0.23 |  | 31.9 | 42.5 | 149 |  | 28.9 | 38.5 | 161
[5 empty] | 3.09 | 0.75 |  | 34.9 | 23.3 | 157 |  | 30.8 | 20.5 | 167 |  |  | 1.03 | 0.11 |  | 30.1 | 60.2 | 144 |  | 28.3 | 56.6 | 158
[5 empty] | 1.02 | 0.11 |  | 31.5 | 63 | 129 |  | 29.5 | 59 | 141 |  |  | 5.17 | 1.94 |  | 46.8 | 18.7 | 163 |  | 40.8 | 16.3 | 172
[5 empty] | 2.06 | 0.41 |  | 39.5 | 39.5 | 147 |  | 35.8 | 35.8 | 158 |  |  | 4.13 | 1.3 |  | 45.4 | 22.7 | 160 |  | 39.7 | 19.9 | 169
|  |  |  | 04 | 2.58 | 0.6 | 420 | 42.4 | 33.9 | 153 | 335 | 37.8 | 30.2 | 164 |  | 04 | 2.58 | 0.6 | 420 | 42.4 | 33.9 | 153 | 335 | 37.8 | 30.2 | 164
[5 empty] | 4.13 | 1.3 |  | 45.4 | 22.7 | 160 |  | 39.7 | 19.9 | 169 |  |  | 2.06 | 0.41 |  | 39.5 | 39.5 | 147 |  | 35.8 | 35.8 | 158
[5 empty] | 5.17 | 1.94 |  | 46.8 | 18.7 | 163 |  | 40.8 | 16.3 | 172 |  |  | 1.02 | 0.11 |  | 31.5 | 63 | 129 |  | 29.5 | 59 | 141
[5 empty] | 2.05 | 0.49 |  | 57.6 | 57.6 | 146 |  | 52.7 | 52.7 | 158 |  |  | 6.19 | 3.16 |  | 69.5 | 23.2 | 164 |  | 62 | 20.7 | 175
[5 empty] | 3.08 | 0.97 |  | 63.1 | 42.1 | 154 |  | 57 | 38 | 166 |  |  | 5.16 | 2.32 |  | 69.1 | 27.6 | 163 |  | 61.2 | 24.5 | 174
|  |  |  | 06 | 4.12 | 1.56 | 620 | 66 | 33 | 158 | 495 | 59.7 | 29.9 | 171 |  | 06 | 4.12 | 1.56 | 620 | 66 | 33 | 158 | 495 | 59.7 | 29.9 | 171
[5 empty] | 5.16 | 2.32 |  | 69.1 | 27.6 | 163 |  | 61.2 | 24.5 | 174 |  |  | 3.08 | 0.97 |  | 63.1 | 42.1 | 154 |  | 57 | 38 | 166
[5 empty] | 6.19 | 3.16 |  | 69.5 | 23.2 | 164 |  | 62 | 20.7 | 175 |  |  | 2.05 | 0.49 |  | 57.6 | 57.6 | 146 |  | 52.7 | 52.7 | 158
[5 empty] | 2.05 | 0.51 |  | 67.1 | 67.1 | 133 |  | 58.1 | 58.1 | 139 |  |  | 8.25 | 5.57 |  | 86.5 | 21.6 | 154 |  | 75.8 | 19 | 163
[5 empty] | 3.08 | 1.02 |  | 75.8 | 50.5 | 143 |  | 68.2 | 45.5 | 153 |  |  | 6.19 | 3.33 |  | 82.6 | 27.5 | 150 |  | 73.4 | 24.5 | 160
|  |  |  | 08 | 4.11 | 1.64 | 845 | 79.3 | 39.7 | 146 | 675 | 71.6 | 35.8 | 158 |  | 08 | 4.11 | 1.64 | 845 | 79.3 | 39.7 | 146 | 675 | 71.6 | 35.8 | 158
[5 empty] | 6.19 | 3.33 |  | 82.6 | 27.5 | 150 |  | 73.4 | 24.5 | 160 |  |  | 3.08 | 1.02 |  | 75.8 | 50.5 | 143 |  | 68.2 | 45.5 | 153
[5 empty] | 8.25 | 5.57 |  | 86.5 | 21.6 | 154 |  | 75.8 | 19 | 163 |  |  | 2.05 | 0.51 |  | 67.1 | 67.1 | 133 |  | 58.1 | 58.1 | 139
[5 empty] | 3.08 | 1.06 |  | 84.6 | 56.4 | 135 |  | 75.9 | 50.6 | 144 |  |  | 10.33 | 8.84 |  | 101.6 | 20.3 | 150 |  | 88.9 | 17.8 | 159
[5 empty] | 4.11 | 1.7 |  | 90.6 | 45.3 | 140 |  | 81.2 | 40.6 | 150 |  |  | 8.24 | 5.76 |  | 98.6 | 24.7 | 147 |  | 86.3 | 21.6 | 156
|  |  |  | 10 | 6.19 | 3.46 | 1040 | 94.6 | 31.5 | 144 | 830 | 84 | 28 | 153 |  | 10 | 6.19 | 3.47 | 1040 | 94.6 | 31.5 | 144 | 830 | 84 | 28 | 153
[5 empty] | 8.24 | 5.76 |  | 98.6 | 24.7 | 147 |  | 86.3 | 21.6 | 156 |  |  | 4.11 | 1.7 |  | 90.6 | 45.3 | 140 |  | 81.2 | 40.6 | 150
[5 empty] | 10.33 | 8.84 |  | 101.6 | 20.3 | 150 |  | 88.9 | 17.8 | 159 |  |  | 3.08 | 1.06 |  | 84.6 | 56.4 | 135 |  | 75.9 | 50.6 | 144
[5 empty] | 4.1 | 1.82 |  | 105.3 | 52.7 | 140 |  | 93.3 | 46.7 | 149 |  |  | 12.37 | 13.21 |  | 119.8 | 20 | 151 |  | 106.7 | 17.8 | 161
[5 empty] | 6.18 | 3.71 |  | 111.6 | 37.2 | 145 |  | 100.4 | 33.5 | 155 |  |  | 10.33 | 9.43 |  | 118.1 | 23.6 | 150 |  | 105 | 21 | 160
|  |  |  | 12 | 8.25 | 6.18 | 1210 | 115.3 | 28.8 | 148 | 970 | 102.8 | 25.7 | 158 |  | 12 | 8.26 | 6.18 | 1210 | 115.3 | 28.8 | 148 | 970 | 102.8 | 25.7 | 158
[5 empty] | 10.33 | 9.43 |  | 118.1 | 23.6 | 150 |  | 105 | 21 | 160 |  |  | 6.18 | 3.71 |  | 111.6 | 37.2 | 145 |  | 100.4 | 33.5 | 155
[5 empty] | 12.38 | 13.21 |  | 119.8 | 20 | 151 |  | 106.7 | 17.8 | 161 |  |  | 4.1 | 1.82 |  | 105.3 | 52.7 | 140 |  | 93.3 | 46.7 | 149
[5 empty] | 4.11 | 2 |  | 109.8 | 54.9 | 133 |  | 100.2 | 50.1 | 143 |  |  | 12.4 | 14.54 |  | 127.9 | 21.3 | 145 |  | 112.2 | 18.7 | 153
[5 empty] | 5.14 | 2.98 |  | 114.8 | 45.9 | 136 |  | 103.5 | 41.4 | 146 |  |  | 10.31 | 10.32 |  | 125.8 | 25.2 | 144 |  | 111.4 | 22.3 | 152
|  |  |  | 14 | 6.18 | 4.08 | 1385 | 118.3 | 39.4 | 139 | 1110 | 106.6 | 35.5 | 149 |  | 14 | 6.18 | 4.08 | 1385 | 118.3 | 39.4 | 139 | 1110 | 106.6 | 35.5 | 149
[5 empty] | 10.31 | 10.32 |  | 125.8 | 25.2 | 144 |  | 111.4 | 22.3 | 152 |  |  | 5.14 | 2.98 |  | 114.8 | 45.9 | 136 |  | 103.5 | 41.4 | 146
[5 empty] | 12.4 | 14.54 |  | 127.9 | 21.3 | 145 |  | 112.2 | 18.7 | 153 |  |  | 4.11 | 2 |  | 109.8 | 54.9 | 133 |  | 100.2 | 50.1 | 143

## HiddenControls (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45
|  | ratings tables |  | Water | [5 empty] | select table |  | Water
|  | size | row | cfm | glycol | [5 empty] | glycol
|  | 1 | 1 |  | 1 | [5 empty] | 1
|  | 02 | 1 ROW | 185 | PROPYLENE | [5 empty] | PROPYLENE
|  | 03 | 2 ROW | 230 | ETHYLENE | [5 empty] | ETHYLENE
04
|  | 06 |  |  | Ethylene | [5 empty] | Ethylene
08
10
12
14
|  | ratings tables |  | Steam |  |  |  |  | These tables would show the cfm choices for the "Rate" sheets when unit size was selected
size
1
02
03
04
06
08
10
12
14

## Cover
Cabinet Unit Heater Selection / Rating Spreadsheet
For Mestek Cabinet Unit Heaters
Designed by M. Girard | Dec. 2010
To run this spreadsheet, macros must be enabled.
Mestek suggests setting Excel's macro security to "Medium"
and selecting "Enable" when the security prompt appears
when opening the spreadsheet.
To set the macro security via the "Tools" menu.
Select "Macro", then "Security", then Medium" and then hit "OK".

## Select-Hot Water (hidden)
Cabinet Unit Heater Hot Water Selection
Input Area
[7 empty] | Imperial Inputs |  |  |  |  | Metric Inputs
|  | Required Capacity |  |  |  |  | Capacity (MBH) |  |  |  |  | Capacity (Watts)
|  | Entering Air Temperature |  |  |  |  | EAT (°F) |  |  |  |  | EAT (°C)
|  | Entering Water Temperature |  |  |  |  | EWT (°F) |  |  |  |  | EWT (°C)
|  | Water Temperature Drop |  |  |  |  | WTD (°F) |  |  |  |  | WTD (°C)
|  | External Static Pressure |  |  |  |  | ESP (Inches H2O) |  |  |  |  | ESP (mm H2O)
|  | Height above Sea Level |  |  |  |  | Altitude (Feet) |  |  |  |  | Altitude (Meters)
|  | Percentage of glycol |  |  |  |  | % Glycol |  |  | Metric inputs overwrite Imperial inputs, leave
blank when using Imperial data.
Output Area
|  | UNIT |  | WATER
Imperial |  | SIZE | GPM | P.D./FT. | CFM | MBH | WTD ºF | FAT ºF | EAT ºF | EWT ºF | COIL
Nearest unit size rated above required MBH | * | [10 empty] | *
| ** | [10 empty] | **
Nearest unit size rated below required MBH | * | [10 empty] | *
| ** | [10 empty] | **
|  | UNIT | Liters/ | WATER
Metric |  | SIZE | Second | P.D./M | M³/min. | Watts | WTD ºC | FAT ºC | EAT ºC | EWT ºC | COIL
Nearest unit size rated above required Watts | * | [10 empty] | *
| ** | [10 empty] | **
Nearest unit size rated below required Watts | * | [10 empty] | *
| ** | [10 empty] | **
* Standard Conditions Catalog Data
** Conditional Unit Data

## Rate-Hot Water (hidden)
Cabinet Unit Heater Hot Water Ratings Calculations
Input Area
| Select unit size | [7 empty] | SIZE
| Select Standard or High Capacity Coil | [7 empty] | COIL
[7 empty] | Imperial Inputs |  |  |  |  | Metric Inputs
| Entering Air Temperature | [5 empty] | EAT (°F) |  |  |  |  | EAT (°C)
| Entering Water Temperature | [5 empty] | EWT (°F) |  |  |  |  | EWT (°C)
| External Static Pressure | [5 empty] | ESP (Inches H2O) |  |  |  |  | ESP (mm H2O)
| Height above Sea Level | [5 empty] | Altitude (Feet) |  |  |  |  | Altitude (Meters)
| Water Temperature Drop | [5 empty] | WTD (°F) |  |  |  |  | WTD (°C)
| Percentage of Glycol | [5 empty] | % Glycol |  |  | Metric inputs overwrite Imperial inputs, leave blank
when using Imperial data.
Output Area
| UNIT |  | WATER
| SIZE | GPM | P.D./FT. | CFM | MBH | WTD ºF | FAT ºF | EAT ºF | EWT ºF | COIL
Imperical Ratings | [10 empty] | Standard Conditions Catalog Data
Conditional Unit Data
| UNIT | Liters/ | WATER
| SIZE | Second | P.D./M | M³/min. | Watts | WTD ºC | FAT ºC | EAT ºC | EWT ºC | COIL
Equivalent Metric Ratings | [10 empty] | Standard Conditions Catalog Data
Conditional Unit Data

## Select-Steam (hidden)
Cabinet Unit Heater Steam Selection
Input Area
[7 empty] | Imperial Inputs |  |  |  | Metric Inputs
|  | Required Capacity |  |  |  |  | Capacity (MBH) |  |  |  | Capacity (Watts)
|  | Entering Air Temperature |  |  |  |  | EAT (°F) |  |  |  | EAT (°C)
|  | Steam Pressure |  |  |  |  | Pressure (PSI) |  |  |  | Pressure (kPa)
|  | External Static Pressure |  |  |  |  | ESP (Inches H20) |  |  |  | ESP (mm H20)
|  | Height above Sea Level (Feet) |  |  |  |  | Altitude (Feet) |  |  |  | Altitude (Meters)
Metric inputs overwrite Imperial inputs, leave Metric inputs blank when using Imperial data.
Output Area
|  | UNIT |  | COND.
Imperial |  | SIZE | EDR | LB/HR | PSI | CFM | MBH | FAT ºF | EAT ºF
Nearest unit size rated above required MBH | * | [8 empty] | *
| ** | [8 empty] | **
Nearest unit size rated below required MBH | * | [8 empty] | *
| ** | [8 empty] | **
|  | UNIT |  | COND.
Metric |  | SIZE | EDR | KG/HR | kPa | M³/min. | Watts | FAT ºC | EAT ºC
Nearest unit size rated above required Watts | * | [8 empty] | *
| ** | [8 empty] | **
Nearest unit size rated below required Watts | * | [8 empty] | *
| ** | [8 empty] | **
* Standard Conditions Catalog Data
** Conditional Unit Data

## Rate-Steam (hidden)
Cabinet Unit Heater Steam Ratings Calculations
Input Area
| Select unit size |  |  | SIZE
[6 empty] | Imperial Inputs |  |  |  | Metric Inputs
| Entering Air Temperature |  |  |  |  | EAT (°F) |  |  |  | EAT (°C)
| Steam Pressure |  |  |  |  | Pressure (PSI) |  |  |  | Pressure (kPa)
| External Static Pressure |  |  |  |  | ESP (Inches H2O) |  |  |  | ESP (mm H2O)
| Height above Sea Level |  |  |  |  | Altitude (Feet) |  |  |  | Altitude (Meters)
Metric inputs overwrite Imperial inputs, leave Metric inputs blank when using Imperial data.
Output Area
| UNIT |  | COND.
| SIZE | EDR | LB/HR | PSI | CFM | MBH | FAT ºF | EAT ºF
Standard Ratings | [8 empty] | Standard Conditions Catalog Data
Conditional Unit Data
Calculations assume High Static Motor option for ESP above .126
| UNIT |  | COND.
| SIZE | EDR | KG/HR | kPa | M³/min. | Watts | FAT ºC | EAT ºC
Equivalent Metric Ratings | [8 empty] | Standard Conditions Catalog Data
Conditional Unit Data
Calculations assume High Static Motor option for ESP above 3.21

## Notes (hidden)
Protected sheets use password: mestek13
Macro's password: mestek13
10/22/2014 | corrected altitude factor in leaving air temp calculation in all macros
2014-11-11 | corrected cfm variable in leaving air temp calculation in all macros.
2015-10-08 | added metric input option to all sheets and metric outputs on sheets that did not have them